## Sheet3
SNAGS | Snag | MAIN_CATEGORY | SUB CATEGORY
Rectifier cabinet door lock is broken |  | DELTA CABINET | DOOR LOCK
cable tray and tower base concrete is cracked |  | CIVIL_WORK | Tower
Fiber cables not arranged properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Lighting rod cable is missing |  | GROUNDING | GROUNDING
shelter 2 step ladder concrete is broken |  | CIVIL_WORK | Indoor Shelter
main gate i getting rusty and concrete support s are cracked |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
extra antenna inside site area |  | EXTRA MATERIAL | EXTRA MATERIAL
Boundary wall is damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower grounding missing |  | GROUNDING | GROUNDING
Fiber cable routing is not OK | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Lighting rod protection cable is not available |  | GROUNDING | GROUNDING
Shelter leakage is there. |  | CIVIL_WORK | Indoor Shelter
shelter legs are angled and not in level. |  | CIVIL_WORK | Indoor Shelter
Vertical ladder is hanging with tower as its base has become damaged. |  | CIVIL_WORK | Cable Tray
Tower is not grounded. |  | GROUNDING | GROUNDING
Fence wire mesh is broken and goats used to get inside the site premises. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Wall is there in front of main site gate. |  | DESIGN ISSUE | DESIGN ISSUE
Tower legs not grounded |  | GROUNDING | GROUNDING
Access way t o RT is not safe \" Ladder and RT\" |  | DESIGN ISSUE | DESIGN ISSUE
No proper pathway to site. |  | CIVIL_WORK | PATHWAY DAMAGE
fiber cables need CR to arrange Routing Properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Tower Paint is required. |  | CIVIL_WORK | Tower
DG alarm cable is not protected. |  | DG ISSUES | DG ISSUES
Tower paint is required. feeder cable ladder is rusty. |  | CIVIL_WORK | Tower
Paint is required. |  | CIVIL_WORK | Tower
Lightning rod is disconnected as earthing strip is broken. |  | GROUNDING | GROUNDING
Feeder cable ladder is rusty. |  | CIVIL_WORK | Cable Tray
Lightning rod earth cable has stolen. |  | GROUNDING | GROUNDING
HSE risk is involved in tower climbing as NPT tower and climbing wire are rusted. |  | CIVIL_WORK | Tower
Emergency light is missing. |  | Emergency Light | Emergency Light
Cables proper arrangement is require. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Front door glass is broken. |  | CIVIL_WORK | Main DB
Lightning rod earth cable is missing. |  | GROUNDING | GROUNDING
Batteries of different ratings are installed with one of the rectifier. | Batteries are in different rating and not Matched | BATTERY BACKUP | BATTERY BACKUP
Both are not grounded. |  | DESIGN ISSUE | DESIGN ISSUE
Fuel hoses are not protected and routed properly. |  | DESIGN ISSUE | DESIGN ISSUE
Cables digging area still open inside site area |  | CIVIL_WORK | Compound Damage
Site boundary wall cracking |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
BTS Room foundation need to maintain |  | CIVIL_WORK | Indoor Shelter
TN Power standby cable is missing |  | DESIGN ISSUE | DESIGN ISSUE
Meter is physically damaged. | Meter is physically damaged | CIVIL_WORK | ACDB
Gate is rusted and requiring paint. |  | CIVIL_WORK | Paint Job
CPRI Cable From 2G cabinet till RT is not protected properly | CPRI cables not arranged properly | CABLE DRESSING | CPRI
Equipment is not installed as per standard. |  | DESIGN ISSUE | DESIGN ISSUE
Cables arrangement for V-Sat equipment is not as per standard/no ducting is there. | VSAT cables not arranged properly | CABLE DRESSING | VSAT
tower paint is required |  | CIVIL_WORK | Paint Job
Shelter body has severe corrosion need to clear |  | CIVIL_WORK | Indoor Shelter
Main gate is rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Vertical ladder is hanging with tower as base is demolished. |  | CIVIL_WORK | Tower
Fibers are required to arrange properly. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Gate is rusted and paint is required. |  | CIVIL_WORK | Paint Job
Smoke sensor is missing |  | DESIGN ISSUE | DESIGN ISSUE
tower painting is required / site is OT Tower |  | CIVIL_WORK | Tower
Tower paint is required |  | CIVIL_WORK | Tower
Tower need to Galvanize and paint |  | CIVIL_WORK | Tower
Whole boundary wall and main gate are rusty due to weather conditions |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Sun cover / canopy is broken |  | CIVIL_WORK | OTHERS
Power meter Box bases completely rusty and be will damage | Power meter Box bases completely rusty-Damaged | CIVIL_WORK | ACDB
Site ground leveling is cracked and damage |  | CIVIL_WORK | Compound Damage
Tower need to galvanize and paint |  | CIVIL_WORK | Tower
Tower base leveling is cracked /OT Tower |  | CIVIL_WORK | Tower
site land leveling is cracked |  | CIVIL_WORK | Compound Damage
Cable tray support is cracked and damage |  | CIVIL_WORK | Cable Tray
Lighting rod cable is disconnected |  | GROUNDING | GROUNDING
Tower paint is required |  | CIVIL_WORK | Tower
Tower physical condition is not OK as its need corrosion cleaning - galvanizing and painting |  | CIVIL_WORK | Tower
Main fence gate is damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
wire mesh boundary wall is rusty and damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Paint is required. |  | CIVIL_WORK | Paint Job
Gate rods are rusted. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Paint is required. |  | CIVIL_WORK | Paint Job
tower painting is required |  | CIVIL_WORK | Tower
tower is rusty and need to galvanize and paint |  | CIVIL_WORK | Tower
Tower Painting is required |  | CIVIL_WORK | Tower
Site compound not secured by any boundary wall /OT is the Host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Label is missing and site ID is written by hand on shelter door |  | LABELING | LABELING
Tower paint is recommended |  | CIVIL_WORK | Paint Job
Tower leg grounding is missing /OT is Host |  | GROUNDING | GROUNDING
wire mesh boundary is damage / OT Is Host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
main gate lock is missing /OT is Host | Site main gate padlock is missing (Omantel as Host) | PADLOCK | PADLOCK/Omantel
Tower legs foundation is damage |  | CIVIL_WORK | Tower
Meter earth pit is damaged. |  | GROUNDING | GROUNDING
Emergency light is not working |  | Emergency Light | Emergency Light
Tower need to paint |  | CIVIL_WORK | Tower
Tower Paint is required |  | CIVIL_WORK | Paint Job
Cable tray is Rusty and tray concrete support is cracked |  | CIVIL_WORK | Cable Tray
tower Bolts &amp; Nuts rusty |  | CIVIL_WORK | Tower
Shelter Body is rusty |  | CIVIL_WORK | Indoor Shelter
BB is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Meter box is physically damaged. | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
Tower paint is required. |  | CIVIL_WORK | Paint Job
DG is dusty. |  | DG ISSUES | DG ISSUES
1 rectifier module is missing. |  | RECTIFIER | RECTIFIER
Fence is damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
There is no proper access pathway to site. |  | CIVIL_WORK | PATHWAY DAMAGE
OD cabinet shelter is not fixed properly even half of the shelter has already gone. |  | DESIGN ISSUE | DESIGN ISSUE
emergency light is faulty ( There is no OD lighting system as per RT BTS rooms Sites design ) |  | DESIGN ISSUE | DESIGN ISSUE
Main tower earth cable is missing |  | GROUNDING | GROUNDING
there is no safe fixed ladder to reach to RT Antenna |  | DESIGN ISSUE | DESIGN ISSUE
Cable tray ladder foundation is cracked. |  | CIVIL_WORK | Cable Tray
Main Gate paint is required. |  | CIVIL_WORK | Paint Job
Smoke detector is not installed. |  | DESIGN ISSUE | DESIGN ISSUE
Smoke detector is not installed. |  | DESIGN ISSUE | DESIGN ISSUE
Smoke detector is not installed. |  | DESIGN ISSUE | DESIGN ISSUE
Cooling system is not working. |  | DELTA CABINET | AIR_CONDITIONER
Fiber cable is not protected. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Earth bus bar is missing. |  | GROUNDING | GROUNDING
Aviation light circuit board is burnt and both of the boxes for supply and board are dirty. | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION LIGHT BOARD
Old alarm is there on controller. |  | RECTIFIER | RECTIFIER
Aviation light system having fault alarm. | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION LIGHT BOARD
Cracks are observed at boundary walls. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Ladder is required to fix. |  | CIVIL_WORK | Cable Tray
Fiber cables are not protected. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
No proper access to overhead antennas. |  | DESIGN ISSUE | DESIGN ISSUE
Bus bar is missing. |  | GROUNDING | GROUNDING
Old alarm is there on controller. |  | RECTIFIER | RECTIFIER
Main fate is rusted and paint is required. |  | CIVIL_WORK | Paint Job
There is no way to the site Hill top Pole so about 5M vertical safe ladder recommended to be install and next distance can be handle by walk |  | DESIGN ISSUE | DESIGN ISSUE
Sand dunes are there inside and outside. |  | CIVIL_WORK | Sand
Lightning rod earth cable is missing. |  | GROUNDING | GROUNDING
Fuel hoses are not protected. |  | DESIGN ISSUE | DESIGN ISSUE
Paint is required. |  | CIVIL_WORK | Paint Job
Fiber cables are required to rout properly. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Gate is rusted/paint is required. |  | CIVIL_WORK | Paint Job
Cracks are there on boundary walls. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Gate is rusted and paint is required. |  | CIVIL_WORK | Paint Job
Lightning rod earth cable is missing. |  | GROUNDING | GROUNDING
Grounding is missing. |  | GROUNDING | GROUNDING
Gate is rusted/paint is required . |  | CIVIL_WORK | Paint Job
Gate is rusted/paint is required. |  | CIVIL_WORK | Paint Job
Boundary fence and razor wire are broken. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Both of cabinets having 1 bank disconnected. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Razor wire is broken. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fiber cables are required to rout properly. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
TN redundant power is missing. |  | DESIGN ISSUE | DESIGN ISSUE
TN redundant power is missing. |  | DESIGN ISSUE | DESIGN ISSUE
TN redundant power is missing. |  | DESIGN ISSUE | DESIGN ISSUE
Cracks are there on boundary walls. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower grounded is missing. |  | GROUNDING | GROUNDING
Fiber cables are not protected. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Shelter is rusted. |  | CIVIL_WORK | Indoor Shelter
Gate is rusted and requiring paint. |  | CIVIL_WORK | Paint Job
Door remains open due to lock fault. |  | OTHERS | DOOR LOCK
Gate is requiring paint. |  | CIVIL_WORK | Paint Job
TN redundant power is missing. |  | DESIGN ISSUE | DESIGN ISSUE
Gate foundation is cracked. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Gate is required to paint. |  | CIVIL_WORK | Paint Job
Smoke detectors in both of cabinets are missing. |  | DESIGN ISSUE | DESIGN ISSUE
Extra material is at site. |  | EXTRA MATERIAL | EXTRA MATERIAL
Gate is requiring paint. |  | CIVIL_WORK | Paint Job
BTS cabinet door lock is faulty. |  | OTHERS | DOOR LOCK
Smoke detectors in both of cabinets are not installed. |  | DESIGN ISSUE | DESIGN ISSUE
RT Access Spiral Ladder is rusted |  | CIVIL_WORK | RT Ladder
Cracks are there. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fence is not properly fixed. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
TN Redundant power is missing. |  | DESIGN ISSUE | DESIGN ISSUE
1 BB is working while other one is disconnected. | One BB string is Zero/Disconnected. | BATTERY BACKUP | BATTERY BACKUP
Batteries of different ratting are utilized with OSN rectifier. | Batteries are in different rating and not Matched | BATTERY BACKUP | BATTERY BACKUP
Non-approved and substandard extension is utilized. |  | DESIGN ISSUE | DESIGN ISSUE
Tower main earth cable is missing |  | GROUNDING | GROUNDING
lighting rod cable is missing |  | GROUNDING | GROUNDING
2 Deng ta battery cells are faulty in first bank and need to replace | One BB string is Zero/Disconnected. | BATTERY BACKUP | BATTERY BACKUP
there is no ladder to reach to RT antenna |  | DESIGN ISSUE | DESIGN ISSUE
RT Antenna ladder is not safe at all and need to replace |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cables are not secured and routed properly. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Emergency light is faulty. |  | Emergency Light | Emergency Light
Tower paint is required. |  | CIVIL_WORK | Tower
There is no ladder for A/C\\\\\\\'s OD units maintenance |  | DESIGN ISSUE | DESIGN ISSUE
RT antenna Ladder is not available and need to install ladder to reach to antenna |  | DESIGN ISSUE | DESIGN ISSUE
there is no ladder to reach to RT antenna |  | DESIGN ISSUE | DESIGN ISSUE
Tower paint is required |  | CIVIL_WORK | Paint Job
Fiber cables are not secured. | Fiber cable are not secured. | CABLE DRESSING | Fiber
Earth pit of energy meter is required to maintain. |  | GROUNDING | GROUNDING
Tower paint is required. |  | CIVIL_WORK | Tower
RT Ladder is Rusty |  | CIVIL_WORK | RT Ladder
4 batteries are weak and fail | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Cracks are there on boundary walls. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Lightning rod earth cable is stolen. |  | GROUNDING | GROUNDING
Shelter repair is required. |  | CIVIL_WORK | Indoor Shelter
fiber cable is not Routed /Protected properly and BBU box need to close as well | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Gate foundation is demolished. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shelter roof repair is required. |  | CIVIL_WORK | Indoor Shelter
Cable is required to rout properly. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
BTS room visual wall cracking |  | CIVIL_WORK | Indoor Shelter
SHDL devises connected to AC directly |  | DESIGN ISSUE | DESIGN ISSUE
Tower painting is required |  | CIVIL_WORK | Paint Job
wire mesh boundary wall have damage part damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
fiber cables need to arrange properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Fence nut &amp; bolts are rusted. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fiber cables are not secured and arranged properly. | Fiber cable are not secured. | CABLE DRESSING | Fiber
cabinets are located at inaccessible location |  | DESIGN ISSUE | DESIGN ISSUE
Cables duct case is missing. |  | OTHERS | OTHERS
Fiber cable is not secured. | Fiber cable are not secured. | CABLE DRESSING | Fiber
Severe seepage is there. |  | CIVIL_WORK | Indoor Shelter
No safe ladder to access antennas. |  | DESIGN ISSUE | DESIGN ISSUE
Deng Ta BB is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Main grounding cable is stolen. |  | GROUNDING | GROUNDING
No proper pathway to site. |  | CIVIL_WORK | PATHWAY DAMAGE
No safe ladder oto access antennas. |  | DESIGN ISSUE | DESIGN ISSUE
FMS device is disconnected. |  | DG ISSUES | DG ISSUES
OD cabinet Shade is missing. |  | DESIGN ISSUE | DESIGN ISSUE
tower cables arrangement is required | Tower Cables arrangement is required | CABLE DRESSING | Tower
Telecom Equipment is not properly fixed. |  | DESIGN ISSUE | DESIGN ISSUE
Cable is not routed with ladder or underground. | Cables not arranged properly | CABLE DRESSING | Cables
site Boundary wall have critical cracking |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fiber cables arrangement is required | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Telecom Device is connected directly with AC |  | DESIGN ISSUE | DESIGN ISSUE
CPRI cable isn&rsquo;t routed properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
no proper access to reach to antenna |  | DESIGN ISSUE | DESIGN ISSUE
both 2 shelter fiber cables need to arrange | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Operational node is connected to AC directly |  | DESIGN ISSUE | DESIGN ISSUE
IF cables are not routed properly. | IF Cables not arranged properly | CABLE DRESSING | IF
site is RT - there is no safe ladder to access RT antenna\'s |  | DESIGN ISSUE | DESIGN ISSUE
Operational node is connected to AC DIRECTLY |  | DESIGN ISSUE | DESIGN ISSUE
RF jumpers are not properly routed. | RF Cables not arranged properly | CABLE DRESSING | CABLE DRESSING
out door foundation are crack |  | CIVIL_WORK | Tower
Site foundation problem( boundary wall/fence foundation is damaged). \r\nfence are damage |  | CIVIL_WORK | Compound Damage
Shelter foundation are crack |  | CIVIL_WORK | Indoor Shelter
Ladder to access AC OD units is not as per HSE standard |  | DESIGN ISSUE | DESIGN ISSUE
No safe ladder is available to access antennas RRU and Ac outdoor unit. |  | DESIGN ISSUE | DESIGN ISSUE
Some of battery cells are faulty. | One BB string is Zero/Disconnected. | BATTERY BACKUP | BATTERY BACKUP
No safe ladder to access OD antenna. |  | DESIGN ISSUE | DESIGN ISSUE
Emergency light is not working . |  | Emergency Light | Emergency Light
Door glass is broken. |  | CIVIL_WORK | Main DB
Main bus bar grounding cable is stolen. |  | GROUNDING | GROUNDING
Fiber cable is not secured. | Fiber cable are not secured. | CABLE DRESSING | Fiber
Equipment is connected with AC power |  | DESIGN ISSUE | DESIGN ISSUE
Equpiment is is connected to AC power directly \r\n |  | DESIGN ISSUE | DESIGN ISSUE
No safe ladder to access antennas. |  | DESIGN ISSUE | DESIGN ISSUE
Only 1 AC installed while there is not backup AC in case of failure. |  | DESIGN ISSUE | DESIGN ISSUE
Battery bank cells are faulty. | One BB string is Zero/Disconnected. | BATTERY BACKUP | BATTERY BACKUP
Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Palm tree site is having some branches to be fixed. |  | CIVIL_WORK | OTHERS
Cable is not arranged on cable tray. | Cable Tray cables not arranged properly | CABLE DRESSING | CABLE DRESSING
Emergency light is not working |  | Emergency Light | Emergency Light
Emergency is missing |  | Emergency Light | Emergency Light
Rented Prime Generator OASIS cables |  | DESIGN ISSUE | DESIGN ISSUE
No safe ladder is there to access antennas and RRUs. |  | DESIGN ISSUE | DESIGN ISSUE
Fuel tank is not grounded. |  | DG ISSUES | DG ISSUES
No safe ladder is there to access antenna. |  | DESIGN ISSUE | DESIGN ISSUE
Main grounding cable is stolen |  | GROUNDING | GROUNDING
Battery bank is dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
couples of batteries is weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
cables are not routed properly | Cables not arranged properly | CABLE DRESSING | Cables
Fuel leakage is there at fuel tank. |  | DG ISSUES | DG ISSUES
FENCE ARE DAMAGE |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site door is broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Seepage is there. |  | CIVIL_WORK | Indoor Shelter
Fiber cable is required to arrange properly. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Cables are required to arrange properly. | Cables not arranged properly | CABLE DRESSING | Cables
BTS room are crack |  | CIVIL_WORK | Indoor Shelter
Fencing rods are damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fiber cable are not secured. | Fiber cable are not secured. | CABLE DRESSING | Fiber
Fiber cables in both of shelters are not secured. | Fiber cable are not secured. | CABLE DRESSING | Fiber
TN redundant power is missing. |  | DESIGN ISSUE | DESIGN ISSUE
Main AC power meter box is dirty &amp; rusted | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
overloaded 15 KV DG so shelter 2nd A/C is on OFF mode due to this Issue - 20kv DG Capacity is recommended |  | DG ISSUES | DG ISSUES
DG capacity 15KV is not compatible with connected site load - One A/C is required to be off during running mode . 20 KV DG capacity is recommended |  | DG ISSUES | DG ISSUES
lightning rod is not available |  | GROUNDING | GROUNDING
one of grounding cable is not available |  | GROUNDING | GROUNDING
lock is missing / OT is a host | Site main gate padlock is missing (Omantel as Host) | PADLOCK | PADLOCK/Omantel
OD units need to clean but surrounding area not safe |  | DESIGN ISSUE | DESIGN ISSUE
one battery cell is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DG canopy has a little rust |  | DG ISSUES | DG ISSUES
Fence are damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
wire mesh fence got damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
external fuel tank is missing grounding |  | DG ISSUES | DG ISSUES
There is no safe way to reach to Air con OD units for maintenance service |  | DESIGN ISSUE | DESIGN ISSUE
There is no access way to reach to OD A/C OD Units for maintenance service |  | DESIGN ISSUE | DESIGN ISSUE
Shelter ground is damaged and has body has wall cracks |  | CIVIL_WORK | Indoor Shelter
Lightning rod cable is missing. |  | GROUNDING | GROUNDING
Tower paint is required. |  | CIVIL_WORK | Paint Job
Cables ladder is rusted. |  | CIVIL_WORK | Cable Tray
Tower is rusted. |  | CIVIL_WORK | Tower
Vertical ladder is rusted. |  | CIVIL_WORK | Cable Tray
Cabinet is rusted. |  | OTHERS | OTHERS
Tower is rusted. |  | CIVIL_WORK | Tower
Feeder cables ladder is damaged. |  | CIVIL_WORK | Cable Tray
Vertical ladder is rusted. |  | CIVIL_WORK | Cable Tray
Radio grounding is missing |  | GROUNDING | GROUNDING
Lightning protector rod cable is missing |  | GROUNDING | GROUNDING
fiber cables protection /Flexible is required | Fiber cable are not secured. | CABLE DRESSING | Fiber
Meter box is dirty and Door meter glass is broken |  | OTHERS | Main DB
BB installation date tag is not available | BB installation date tag is not available | BATTERY BACKUP | LABELING
Distribution panel is placed at very narrow space /Difficult to fix in case of required maintenance |  | DESIGN ISSUE | DESIGN ISSUE
fuel tank is missing grounding |  | DG ISSUES | DG ISSUES
site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Fiber cables not protected properly /Flexible is required | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Logbook is not available at site |  | LOG BOOK | LOG BOOK
IF Cables not protected properly | IF Cables not arranged properly | CABLE DRESSING | IF
power meter box glass is broken |  | OTHERS | Main DB
Lightening protection strip is broken |  | GROUNDING | GROUNDING
tower painting is required |  | CIVIL_WORK | Tower
power meter box is rusted | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
PBc6500 Rectifier are available inside |  | DESIGN ISSUE | DESIGN ISSUE
Entire fence is rusted/damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Feeder cables ladder is rusted. |  | CIVIL_WORK | Cable Tray
RRUs grounding is stolen/missing. |  | GROUNDING | GROUNDING
No safe ladder to access antennas. |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cables are not secured. | Fiber cable are not secured. | CABLE DRESSING | Fiber
Tower leg grounding is disconnected |  | GROUNDING | GROUNDING
No safe ladder is there. |  | DESIGN ISSUE | DESIGN ISSUE
Some of battery cells are faulty. | One BB string is Zero/Disconnected. | BATTERY BACKUP | BATTERY BACKUP
Cable tray basement broken |  | CIVIL_WORK | Cable Tray
Fiber cables are not secured. | Fiber cable are not secured. | CABLE DRESSING | Fiber
there is no safe ladder to move up to antenna only long steel ladder available |  | DESIGN ISSUE | DESIGN ISSUE
fiber cable not protected properly rand some cable need to arrange properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Fiber cable is not secured. | Fiber cable are not secured. | CABLE DRESSING | Fiber
No safe ladder to reach antenna end |  | DESIGN ISSUE | DESIGN ISSUE
No proper ladder to reach antenna end |  | DESIGN ISSUE | DESIGN ISSUE
Lighting rod is missing |  | GROUNDING | GROUNDING
No safe ladder to reach antenna end |  | DESIGN ISSUE | DESIGN ISSUE
cables are not properly routed on cable tray | Cables not arranged properly | CABLE DRESSING | Cables
Fiber cables are not protected with flexible pipe | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Other than Huawei rectifier. Emerson. |  | DESIGN ISSUE | DESIGN ISSUE
Lightning rod cable is missing. |  | GROUNDING | GROUNDING
FMS device is disconnected. |  | DG ISSUES | DG ISSUES
Smoke detector is missing. |  | DESIGN ISSUE | DESIGN ISSUE
Lightning rod cable is stolen. |  | GROUNDING | GROUNDING
No safe ladder available to reach antenna end |  | DESIGN ISSUE | DESIGN ISSUE
Site is covered with sand |  | CIVIL_WORK | Sand
Site is covered with sand |  | CIVIL_WORK | Sand
ASCOT DG is not working -HYBRID DG |  | DG ISSUES | DG ISSUES
Main power cable not routed / protected properly |  | DG ISSUES | DG ISSUES
ASCOT DG is not working |  | DG ISSUES | DG ISSUES
Dismantled DG- Fuel Tank is available at Site |  | DG ISSUES | DG ISSUES
Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main gate is damage (OT as a Host ) |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
alarms for OSN shelter need to be configured after hybrid swapped. |  | DESIGN ISSUE | DESIGN ISSUE
Sit ID Label is missing |  | LABELING | LABELING
Cable ladder is required for OD fiber cable arrangement |  | DESIGN ISSUE | DESIGN ISSUE
Site ID Label is missing |  | LABELING | LABELING
Emergency light is not working |  | Emergency Light | Emergency Light
Main power cable from DG to ATS need to secure |  | DG ISSUES | DG ISSUES
BB installation date tag is not available | BB installation date tag is not available | BATTERY BACKUP | LABELING
Power DB front cover can not be installed due to ODF rack infront of DB-fiber cable can be damage during installation |  | DESIGN ISSUE | DESIGN ISSUE
Fence and main gate not available |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Intudar alarm not working-door sensor not installed |  | DESIGN ISSUE | DESIGN ISSUE
DG fuel tank is not grounded |  | DG ISSUES | DG ISSUES
DG external fuel tank and pipe rusted and need to paint and DG need to clean from internal side |  | DG ISSUES | DG ISSUES
E1 cable from OSN to ODF DDF not properly routed | E1 Cables not arranged properly | CABLE DRESSING | CABLE DRESSING
DG canopy is damaged |  | DG ISSUES | DG ISSUES
fiber cable need to arrange properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Ladder Main gate is damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
fiber cables are not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Batteries of different ratings are installed. | Batteries are in different rating and not Matched | BATTERY BACKUP | BATTERY BACKUP
1 Battery cell is physically damage. | Battery cell is physically damage | BATTERY BACKUP | BATTERY BACKUP
BB is zero mentioned in logbook. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Stair is rusted and damaged. |  | CIVIL_WORK | OTHERS
DP is rusted. | DP completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
Gate rods are rusted and damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fence nut/bolts are rusted. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
There is no proper access pathway. |  | CIVIL_WORK | PATHWAY DAMAGE
Fiber cable is not secured. | Fiber cable are not secured. | CABLE DRESSING | Fiber
Fence is not properly painted. |  | CIVIL_WORK | Paint Job
BB is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DP hings is broken and repaired improperly/Need to fix as per standard. | DP completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
site grounding level is not OK and need to maintain |  | CIVIL_WORK | Compound Damage
Site Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
No proper pathway to reach Antenna &amp; rru |  | DESIGN ISSUE | DESIGN ISSUE
Batteries of different ratings are installed. | Batteries are in different rating and not Matched | BATTERY BACKUP | BATTERY BACKUP
Emergency light is not working |  | Emergency Light | Emergency Light
Fiber cables are not properly arrange | Fiber cables not arranged properly | CABLE DRESSING | Fiber
DG is rusted. |  | DG ISSUES | DG ISSUES
Fiber cables in both of shelters are mo secured. | Fiber cable are not secured. | CABLE DRESSING | Fiber
Emergency light is not working |  | Emergency Light | Emergency Light
Cable are not properly routed | Cables not arranged properly | CABLE DRESSING | Cables
wire razor are damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Equipment is connected on ac power |  | DESIGN ISSUE | DESIGN ISSUE
RT Antenna is not accessable for maintenance |  | DESIGN ISSUE | DESIGN ISSUE
RT Pole Nuts are rusted |  | CIVIL_WORK | Antenna Pole
Rental DG main power cable is not protected &amp; Routed properly |  | DG ISSUES | DG ISSUES
External Fuel tank is dirty and not grounded |  | DG ISSUES | DG ISSUES
tower is rusted and need to paint |  | CIVIL_WORK | Tower
couples of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Boundary wall are crack |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Boundary wall or Fence is not available at site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
No proper ladder to reach Ac outdoor unit |  | DESIGN ISSUE | DESIGN ISSUE
No safe ladder to reach antenna &amp; rru end |  | DESIGN ISSUE | DESIGN ISSUE
BTS room are crack |  | CIVIL_WORK | Indoor Shelter
No safe ladder to reach Antenna &amp; rru end |  | DESIGN ISSUE | DESIGN ISSUE
Tower paint is required |  | CIVIL_WORK | Paint Job
Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
O/D cabinet door lock is not working |  | OTHERS | OTHERS
No proper ladder to reach Ac outdoor unit |  | DESIGN ISSUE | DESIGN ISSUE
Cable tray damage. |  | CIVIL_WORK | Cable Tray
battery have leakage issuse | Battery have leakage issuse | BATTERY BACKUP | BATTERY BACKUP
Batteries terminal required to maintenance |  | OTHERS | OTHERS
Tower leg groundings is missing |  | GROUNDING | GROUNDING
Tower Ladder basement foundation demolished due to wadi |  | CIVIL_WORK | Tower
fiber cable are not arrange properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
No proper pathway to reach ac outdoor unit |  | DESIGN ISSUE | DESIGN ISSUE
Emergency light is not working |  | Emergency Light | Emergency Light
No proper ladder to reach Antenna &amp; rru |  | DESIGN ISSUE | DESIGN ISSUE
No proper pathway to reach Antenna &amp; rru |  | DESIGN ISSUE | DESIGN ISSUE
Wire razor are damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Power cable is required to rout properly. | Main Power Cables not arranged properly | CABLE DRESSING | Power Cable
No safe ladder to access antennas. |  | DESIGN ISSUE | DESIGN ISSUE
Lighting rod cable is missing. |  | GROUNDING | GROUNDING
Rectifier in OSN shelter is connected thru power socket. |  | DESIGN ISSUE | DESIGN ISSUE
Lightning rod earth cable is missing. |  | GROUNDING | GROUNDING
Lighting rod earth cable is missing. |  | GROUNDING | GROUNDING
Rectifier is module is not fixed properly. |  | DESIGN ISSUE | DESIGN ISSUE
OD unit connection plate is missing. |  | OTHERS | OTHERS
PDB cover is removed. |  | OTHERS | OTHERS
shelter wall pasted poster need to remove and paint shelter body |  | CIVIL_WORK | Paint Job
Rdg Power cable are not properly routed |  | DG ISSUES | DG ISSUES
Door open alarm are not reported in noc |  | DESIGN ISSUE | DESIGN ISSUE
High temp Alarm are not reported in noc |  | DESIGN ISSUE | DESIGN ISSUE
Air-con alarm are not reported in noc |  | DESIGN ISSUE | DESIGN ISSUE
Site Cleaning is required |  | OTHERS | OTHERS
BB installation date tag is not available | BB installation date tag is not available | BATTERY BACKUP | LABELING
Batteries humidity pipes are missing | Batteries humidity pipes are missing | BATTERY BACKUP | OTHERS
Site Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
OSN shelter is not connected with Standby DG due to DG capacity issue |  | DESIGN ISSUE | DESIGN ISSUE
Couples of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Seepage and Crack are there inside shelter room. |  | CIVIL_WORK | Indoor Shelter
Fence razor wire is broken. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Emergency light is not working |  | Emergency Light | Emergency Light
Fuel tanks is rusted |  | DG ISSUES | DG ISSUES
Cabinet suncover is rusted |  | CIVIL_WORK | OTHERS
Aviation light panel damaged | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION LIGHT BOARD
Main power cable not installed properly inside the cabinet | Main Power Cables not arranged properly | CABLE DRESSING | Power Cable
unused Ericsson rectifier and voltage regulator device available inside the cabinet |  | EXTRA MATERIAL | EXTRA MATERIAL
Cabinet sun shield is rusted |  | CIVIL_WORK | OTHERS
Aviation light panel damaged | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION LIGHT BOARD
main power cable not routed /protected properly | Main Power Cables not arranged properly | CABLE DRESSING | Power Cable
DP panel damaged |  | OTHERS | OTHERS
Main gate is damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Lightning rod cable is damage |  | GROUNDING | GROUNDING
tower leg grounding is disconnected |  | GROUNDING | GROUNDING
DG body and external tank need some paint |  | DG ISSUES | DG ISSUES
door lock is damage | Site main gate padlock is missing | PADLOCK | PADLOCK
box is rusted and need paint |  | OTHERS | OTHERS
MF200 fire control panel is faulty |  | FIRE EQUIPMENT | Fire Panel
Generator alarm is not installed properly |  | DG ISSUES | DG ISSUES
OD pipes duct is damage |  | OTHERS | OTHERS
power meter box door is not OK and base is rusted | Power meter Box and bases completely rusty-Damaged | CIVIL_WORK | ACDB
Rectifier module is missing |  | RECTIFIER | RECTIFIER
Main gate lock is missing /OT Site | Site main gate padlock is missing (Omantel as Host) | PADLOCK | PADLOCK/Omantel
Housekeeping hazard need to be clear /Shared OT Site |  | HOUSEKEEPING | HOUSEKEEPING/Omantel
GPS bracket is tighten by plastic tie wrap |  | OTHERS | OTHERS
Tower Ladder is rusted /OT is a host |  | CIVIL_WORK | Tower
shelter body need to maintain |  | CIVIL_WORK | Indoor Shelter
Emergency light is not working |  | Emergency Light | Emergency Light
No proper ladder to reach antenna &amp; rru |  | DESIGN ISSUE | DESIGN ISSUE
No safe ladder to reach Antenna &amp; rru |  | DESIGN ISSUE | DESIGN ISSUE
Emergency light is not working |  | Emergency Light | Emergency Light
Emergency light is not working |  | Emergency Light | Emergency Light
site log book is missing |  | LOG BOOK | LOG BOOK
fiber cable need to be protected by light flexible pipe | Fiber cable are not secured. | CABLE DRESSING | Fiber
All grounding cables have been cut |  | GROUNDING | GROUNDING
RT Poles room construction got damage and dedicated civil team is required for treatment |  | CIVIL_WORK | OTHERS
A/C OD cable duct rusted |  | OTHERS | OTHERS
poles grounding is missing |  | GROUNDING | GROUNDING
cable tray is rusted |  | CIVIL_WORK | Cable Tray
RT poles bolts rusted |  | CIVIL_WORK | Antenna Pole
fiber cable not routed and protected properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
emergency light is not working |  | Emergency Light | Emergency Light
BTS Room cracking and seepage |  | CIVIL_WORK | Indoor Shelter
OD unites pipes not isolated properly | OD A/C unites pipes not isolated properly | AIR_CONDITIONER | AIR_CONDITIONER
fire panel is showing common Faulty alarm |  | FIRE EQUIPMENT | Fire Panel Battery
BB installation date is not available | BB installation date tag is not available | BATTERY BACKUP | LABELING
Log book is not available |  | LOG BOOK | LOG BOOK
RT poles missing grounding cable |  | GROUNDING | GROUNDING
outside shelter feeders missing labeling |  | LABELING | LABELING
Other than Huawei rectifier at site. |  | DESIGN ISSUE | DESIGN ISSUE
2 battery cells cover is missing |  | OTHERS | OTHERS
TN redundant power is missing. |  | DESIGN ISSUE | DESIGN ISSUE
site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
VSAT Dish not connected to ground |  | DESIGN ISSUE | DESIGN ISSUE
Fire panel is showing Common failure alarm |  | FIRE EQUIPMENT | Fire Panel Battery
Fire panel is not working. |  | FIRE EQUIPMENT | Fire Panel Battery
Meter door hings is broken. |  | OTHERS | OTHERS
Tower paint is required. |  | CIVIL_WORK | Paint Job
Meter box lock is broken. |  | OTHERS | OTHERS
Cables are not properly arrange | Cables not arranged properly | CABLE DRESSING | Cables
Fuse is removed and cable is directly connected to meter | Fuse is removed and cable is directly connected to meter | CABLE DRESSING | CABLE DRESSING
Shelter OD earth bar main cable is not available |  | GROUNDING | GROUNDING
Main Gate lock is missing - OT is HOST | Site main gate padlock is missing (Omantel as Host) | PADLOCK | PADLOCK/Omantel
Main grounding bar is damage and cable is stolen |  | GROUNDING | GROUNDING
site grounding level is fallen down is some area |  | CIVIL_WORK | Compound Damage
Main power meter is damage | Main Power Cables not arranged properly | CABLE DRESSING | Power Cable
door has minor damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
OD units pipe duct cover is missing. |  | OTHERS | OTHERS
Old alarms are there on controller. |  | RECTIFIER | RECTIFIER
Lightning rod cable is stolen. |  | GROUNDING | GROUNDING
Site Batteries are stolen. | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
No safe ladder to access overhead antennas. |  | DESIGN ISSUE | DESIGN ISSUE
Cracks are there on room walls. |  | CIVIL_WORK | Indoor Shelter
Almost whole cable tray is required to fix. |  | CIVIL_WORK | Cable Tray
Wimax cabinet battery cells are faulty. | TDD/WiMax Battery Backup is Zero/Dead | BATTERY BACKUP | TDD/WiMax
TN redundant power is missing. |  | DESIGN ISSUE | DESIGN ISSUE
Lightning rod cable is stolen. |  | GROUNDING | GROUNDING
Lightning rod cable is missing. |  | GROUNDING | GROUNDING
Site batteries are stolen. | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Boundary wall paint is required. |  | CIVIL_WORK | Paint Job
TN redundant power is missing. |  | DESIGN ISSUE | DESIGN ISSUE
Lightning rod cable is stolen. |  | GROUNDING | GROUNDING
Shelter is not in level. |  | CIVIL_WORK | Indoor Shelter
Batteries are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Couples of battery is weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
No safe ladder to reach Ac outdoor units |  | DESIGN ISSUE | DESIGN ISSUE
Room have seapage &amp; crack issuse |  | CIVIL_WORK | Indoor Shelter
Cables are not properly routed | Cables not arranged properly | CABLE DRESSING | Cables
Different capacity installed battery backup battery strings | Batteries are in different rating and not Matched | BATTERY BACKUP | BATTERY BACKUP
couples of batteries are dead | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not secured | Fiber cable are not secured. | CABLE DRESSING | Fiber
SDH cables are not properly arrange | SDH Cables not arranged properly | CABLE DRESSING | CABLE DRESSING
Room have seapage issuse |  | CIVIL_WORK | Indoor Shelter
Equipment is connected on Ac power |  | DESIGN ISSUE | DESIGN ISSUE
Shelter room ceiling is required to fix. |  | CIVIL_WORK | Indoor Shelter
Batteries of different ratings are installed in same bank. | Batteries are in different rating and not Matched | BATTERY BACKUP | BATTERY BACKUP
Battery cells are faulty. | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Battery cells are faulty. | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Sec-3 RRUs main grounding cable is missing. |  | GROUNDING | GROUNDING
Fiber cables are required to arrange properly. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
No Honeywell is installed in room. |  | DESIGN ISSUE | DESIGN ISSUE
Substandard power extension is used to power up rectifier. |  | DESIGN ISSUE | DESIGN ISSUE
Access pathway is damaged. |  | CIVIL_WORK | PATHWAY DAMAGE
Fiber cables are not secured | Fiber cable are not secured. | CABLE DRESSING | Fiber
SDH cables are not properly routed | SDH Cables not arranged properly | CABLE DRESSING | CABLE DRESSING
Tower grounding leg is missing |  | GROUNDING | GROUNDING
Fiber cables are not properly arrange | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Couple of batteries are week | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Room have seapage issuse |  | CIVIL_WORK | Indoor Shelter
Couple of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Fiber cables is not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Foundation base chuck nuts are rusted |  | CIVIL_WORK | Indoor Shelter
Site yellow label ID required. |  | LABELING | LABELING
OD A/C pipes duct is rusted | OD A/C pipes duct is rusted | AIR_CONDITIONER | AIR CONTIONER ODU
main power meter box damage and rusted | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
Main power cable path is not safe and need rectification action ASAP | Main Power Cables not arranged properly | CABLE DRESSING | Power Cable
Pathway need to repair |  | CIVIL_WORK | PATHWAY DAMAGE
tower paint required |  | CIVIL_WORK | Paint Job
Tower leg grounding is missing |  | GROUNDING | GROUNDING
All batteries are stolen | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
fence are damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Fence must be repaired and can be open easily as Padlock is useless |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower paint is required. |  | CIVIL_WORK | Tower
Tower painting is required |  | CIVIL_WORK | Tower
IF cables need to arrange properly | IF cables not arranged properly | CABLE DRESSING | IF
External fuel tank is rusty and need to paint |  | DG ISSUES | DG ISSUES
On load DG missing is observed. Needs health check |  | DG ISSUES | DG ISSUES
Fuel pipes are not routed and protected properly. |  | DG ISSUES | DG ISSUES
Emergency light is not working |  | Emergency Light | Emergency Light
main gate pad lock is faulty |  | OTHERS | DOOR LOCK
Gate is rusted/requiring paint. |  | CIVIL_WORK | Paint Job
One of door locks is broken. | Power meter Box door locks are broken | CIVIL_WORK | ACDB
Bus Bars are missing. |  | GROUNDING | GROUNDING
Lighting rod cable is cut |  | GROUNDING | GROUNDING
RT ladder Hand rail is broken and ladder is rusty |  | CIVIL_WORK | RT Ladder
ladder cable arrangement is required | Cables not arranged properly | CABLE DRESSING | Cables
6th Energy device is powered off. |  | OTHERS | OTHERS
Fuel pipe lines are rusted. |  | DG ISSUES | DG ISSUES
ATS panel is not sealed. |  | DG ISSUES | DG ISSUES
Iron duct case is missing. |  | OTHERS | OTHERS
Alarm cables are required to arrange. | Alarm cables not arranged properly | CABLE DRESSING | CABLE DRESSING
6th Energy devices are powered off. |  | OTHERS | OTHERS
Shelter paint is required. |  | CIVIL_WORK | Indoor Shelter
Meter box locks are broken. | Power meter Box door locks are broken | CIVIL_WORK | ACDB
RT Ladder and some pole bolts are rusted |  | CIVIL_WORK | Antenna Pole
Battery backup banks dead and need to replace | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
OD tray cable not arranged properly | OD cable not arranged properly | CABLE DRESSING | CABLE DRESSING
Fiber cable is not routed/secured properly with conduit piper. | Fiber cable are not secured. | CABLE DRESSING | Fiber
couples of batteries is weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Emergency light is not working |  | Emergency Light | Emergency Light
Lightning rod cable is missing. |  | GROUNDING | GROUNDING
Fuel tank is not grounded. |  | DG ISSUES | DG ISSUES
Lightning rod cable is not connected with grounding system. |  | GROUNDING | GROUNDING
Fuel tank top is rusted and required to paint. |  | DG ISSUES | DG ISSUES
Fuel tank is not grounded. |  | DG ISSUES | DG ISSUES
Main power meter box is totally rusted | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
DG external tank with fuel pipes are rusted |  | DG ISSUES | DG ISSUES
No safe ladder to reach A/c outdoor units |  | DESIGN ISSUE | DESIGN ISSUE
Equipment is connected on AC power |  | DESIGN ISSUE | DESIGN ISSUE
Main gate rusted |  | CIVIL_WORK | Paint Job
Wire razor are damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Fiber cable is not arrange properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Fiber cables are not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
All batteries are swelled | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
batteries have zero backup | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Razor wire is damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Fiber cables are not arrange properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Fiber cables are not arrange properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Equipment is connected on ac power |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cable is not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Fiber cables are not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Osn power cables is not properly routed | Main Power Cables not arranged properly | CABLE DRESSING | Power Cable
Equipment is connected on AC power |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cables are not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
IF &amp; Fiber cables not protected properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
fiber cables not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Fiber cables nor properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Emerson rectifier is running at site |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cable is not routed /protected properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
operational node is connected directly to AC |  | DESIGN ISSUE | DESIGN ISSUE
No proper pathway to access the site and tower as well . |  | CIVIL_WORK | PATHWAY DAMAGE
Compound damaged |  | CIVIL_WORK | Compound Damage
No concrete base for gas tank |  | CIVIL_WORK | OTHERS
pathway need repairing |  | CIVIL_WORK | PATHWAY DAMAGE
Main Fence gate and boundary wall broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Pathway need repairing |  | CIVIL_WORK | PATHWAY DAMAGE
Fiber cable is not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Fiber cable is not properly routed | Fiber cable are not secured. | CABLE DRESSING | Fiber
Ericsson PBC 6500 Rectifier is available |  | DESIGN ISSUE | DESIGN ISSUE
All batteries are dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Generated High temp Alarm is not reported to FO |  | EXTERNAL ALARM | EXTERNAL ALARM
generated A/C alarm is not resorting to FO |  | EXTERNAL ALARM | EXTERNAL ALARM
DG external tank is rusted and need paint |  | DG ISSUES | DG ISSUES
one main grounding cable is cut |  | GROUNDING | GROUNDING
only one CP Phase is working at site |  | OTHERS | OTHERS
BB installation date tag is missing | BB installation date tag is not available | BATTERY BACKUP | LABELING
Extra Fuel Tank is available inside site penises |  | DG ISSUES | DG ISSUES
Power cable is burnt |  | OTHERS | OTHERS
OD BTS sin cover is damaged |  | OTHERS | OTHERS
Fiber cable are not secured | Fiber cable are not secured. | CABLE DRESSING | Fiber
Couples of battery are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Emerson rectifier is running at shelter |  | DESIGN ISSUE | DESIGN ISSUE
Extra portable DG available at site premises |  | DG ISSUES | DG ISSUES
Fiber cables not routed /Protected properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
BBS2000 and Emerson rectifier is running at site |  | DESIGN ISSUE | DESIGN ISSUE
4 Batteries have leakage | One BB string is Zero/Disconnected. | BATTERY BACKUP | BATTERY BACKUP
Fiber cables not routed and arranged properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Ericsson rectifier is running at site |  | DESIGN ISSUE | DESIGN ISSUE
BTS room major seepage is there |  | CIVIL_WORK | Indoor Shelter
there is no security fence |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
fiber cables not protected properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
BTS Room seepage is there |  | CIVIL_WORK | Indoor Shelter
Fiber cables not arranged properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
fiber cables not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Fiber cables not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Fiber cables not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Emerson rectifier is running at site |  | DESIGN ISSUE | DESIGN ISSUE
RT Site have no proper access for Antenna |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cable not properly routed /protected | Fiber cable are not secured. | CABLE DRESSING | Fiber
external fuel tank need to clean |  | DG ISSUES | DG ISSUES
Fiber cables nor properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Cabinet smoke sensor is missing |  | DESIGN ISSUE | DESIGN ISSUE
Lightning rod earth cable is stolen. |  | GROUNDING | GROUNDING
fiber cable are not arrange properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
need to install RT ladder for RT antenna access |  | DESIGN ISSUE | DESIGN ISSUE
Lighting rod is missing. |  | GROUNDING | GROUNDING
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Tower leg grounding is missing\r\n |  | GROUNDING | GROUNDING
Rectifier controller screen is faulty &amp; one module is faulty |  | RECTIFIER | Rectifeir Module
2 rectifier modules showing alarms |  | RECTIFIER | Rectifeir Module
Wire razor are Rusted and damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Other than Huawei rectifier at site. |  | DESIGN ISSUE | DESIGN ISSUE
Battery terminal cap is missing | Battery terminal cap is missing | BATTERY BACKUP | OTHERS
power cable is not routed &amp; protected safely |  | CIVIL_WORK | OTHERS
DG and external tank not grounded |  | DG ISSUES | DG ISSUES
Fiber cables are not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Site Access Pathway is damage |  | CIVIL_WORK | PATHWAY DAMAGE
Extra disconnected external Fuel tank available at site premises |  | DG ISSUES | DG ISSUES
A/C Panel Off on switch Not available | A/C Panel Off-On switch Not available | AIR_CONDITIONER | AIR_CONDITIONER
Site main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Batteries is missing | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Delta cooling system is not producing cooling |  | DELTA CABINET | AIR_CONDITIONER
Fiber cable is not secured | Fiber cable are not secured. | CABLE DRESSING | Fiber
Fiber cable is not secured | Fiber cable are not secured. | CABLE DRESSING | Fiber
Fiber cables are not properly routed on cable tray | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Shelter is rusted |  | CIVIL_WORK | Indoor Shelter
Tower leg grounding is missing |  | GROUNDING | GROUNDING
SDH cables are not properly arrange | SDH Cables not arranged properly | CABLE DRESSING | CABLE DRESSING
Meter box base is damage | Power meter Box bases completely rusty-Damaged | CIVIL_WORK | ACDB
fiber cable need to protect and route properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Emergency light is not working |  | Emergency Light | Emergency Light
Emerson Rectifier are available |  | DESIGN ISSUE | DESIGN ISSUE
Couple of battery is weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Emerson rectifier are available |  | DESIGN ISSUE | DESIGN ISSUE
Emergency light is not working |  | Emergency Light | Emergency Light
Room have seepage issuse |  | CIVIL_WORK | Indoor Shelter
Tower painting is required - OmanTel as Host |  | CIVIL_WORK | Paint Job
Main gate is fully rusted and need to replace |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Tower ladder base is crack |  | CIVIL_WORK | Tower
Fiber cable are not secured | Fiber cable are not secured. | CABLE DRESSING | Fiber
Fiber cables and SDH cables is not arrange properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
No safe ladder to reach antenna &amp; air condition |  | DESIGN ISSUE | DESIGN ISSUE
cleaning is required\\r\\n(dismantle inverter) |  | OTHERS | OTHERS
Main AC power meter box is completely rusted and damage need to replace | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
Battery backup banks are stolen | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Smoke sensor is damage |  | OTHERS | OTHERS
Fiber cables is not secured | Fiber cable are not secured. | CABLE DRESSING | Fiber
Emergency light is not working |  | Emergency Light | Emergency Light
Battery back up banks are very weak and need to replace | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Emerson rectifier is running at site |  | DESIGN ISSUE | DESIGN ISSUE
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Fiber cables are not properly arrange | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Batteries is missing | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Batteries is missing | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Cable tray is fallen down |  | CIVIL_WORK | Cable Tray
Fiber cable is not secured | Fiber cable are not secured. | CABLE DRESSING | Fiber
Emergency light is not working |  | Emergency Light | Emergency Light
Wire mesh and fencing paint is required |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower leg grounding is missing |  | GROUNDING | GROUNDING
there is no access ladder to RT Antenna |  | DESIGN ISSUE | DESIGN ISSUE
No safe ladder available to reach antenna &amp; RRU end |  | DESIGN ISSUE | DESIGN ISSUE
Couples of batteries are dead | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Fiber cables is not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Tower Leg grounding is missing |  | GROUNDING | GROUNDING
Batteries is missing | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
No Proper permanent ladder available to access antenna\r\n |  | DESIGN ISSUE | DESIGN ISSUE
Tower paint work required |  | CIVIL_WORK | Paint Job
Tower base has cracks |  | CIVIL_WORK | Tower
Tower nuts and bolts are rusted |  | CIVIL_WORK | Tower
One AC not working need to be replaced | One A/C not working need to be replaced | AIR_CONDITIONER | AIR_CONDITIONER
need to paint and have rusted bolts |  | CIVIL_WORK | Tower
Fiber cables is not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Couple of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Fiber cables is not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Different capacity installed battery backup battery strings\r\n | Batteries are in different rating and not Matched | BATTERY BACKUP | BATTERY BACKUP
Couples of batteries are dead | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
NO safe ladder to reach antenna &amp; rru end |  | DESIGN ISSUE | DESIGN ISSUE
couples of batteries are swelled | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Batteries are dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Fiber cables is not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
B/C infinity link is not properly installed in outdoor cabinet |  | DESIGN ISSUE | DESIGN ISSUE
Couples of batteries is weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Couple of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Site main gate is damage and lock is missing |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Bus bar Grounding cable is missing |  | GROUNDING | GROUNDING
No safe ladder to reach Antenna and rru |  | DESIGN ISSUE | DESIGN ISSUE
Ericsson pbc 6500 rectifier is available |  | DESIGN ISSUE | DESIGN ISSUE
Site main gate lock hook is damage and lock is missing |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shelter body is rusted |  | CIVIL_WORK | Indoor Shelter
Main gate and fencing is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
RDU tower lower section have major rusted and start bending -Civil corrective action is required ASAP . |  | CIVIL_WORK | Antenna Pole
No fence and gate is at site. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
tower need to paint |  | CIVIL_WORK | Paint Job
NO power redundancy for TN |  | DESIGN ISSUE | DESIGN ISSUE
Traffic node power connected through rectifier module- need rectifier |  | DESIGN ISSUE | DESIGN ISSUE
Earthing bars need greasing |  | OTHERS | OTHERS
Site Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
OD Earthing cables need greasing |  | OTHERS | OTHERS
No safe ladder to reach A/c outdoor unit |  | DESIGN ISSUE | DESIGN ISSUE
Emergency light is not working |  | Emergency Light | Emergency Light
Emergency light is not working |  | Emergency Light | Emergency Light
Tower leg grounding is damage. |  | GROUNDING | GROUNDING
Wire razor is damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Ericsson rectifier is running at site |  | DESIGN ISSUE | DESIGN ISSUE
External Alarms not Reported due to NPU3C installed can\'t configure alarms at TN6P |  | DESIGN ISSUE | DESIGN ISSUE
Ericsson Outdoor Cabinet AC Faulty | Ericsson Outdoor Cabinet AC Faulty | AIR_CONDITIONER | OD CABINET AIR CON
Cabinet Installed at nearby tower leg. Cabinet Door Not Proper Open |  | DESIGN ISSUE | DESIGN ISSUE
Site Fence is missing |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site Pathway is damage |  | CIVIL_WORK | PATHWAY DAMAGE
All grounding cables and earth pit stolen |  | GROUNDING | GROUNDING
NO proper pathway to reach antenna &amp; rru end |  | DESIGN ISSUE | DESIGN ISSUE
site main gate is rusted and have a major damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Wire mesh boundary wall have damage part |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
No safe and proper ladder to reach antenna &amp; rru end |  | DESIGN ISSUE | DESIGN ISSUE
BTS lock is not working |  | OTHERS | OTHERS
Site was fully covered with Sand /OT is a host |  | CIVIL_WORK | Sand
Site Area is covered with sand /OT Shared site |  | CIVIL_WORK | Sand
Site Access Pathway is damage |  | CIVIL_WORK | PATHWAY DAMAGE
One fuse is missing |  | OTHERS | OTHERS
lightning protection rod cable is missing |  | GROUNDING | GROUNDING
one rectifier module is faulty |  | RECTIFIER | RECTIFIER
Emerson rectifier is running at site |  | DESIGN ISSUE | DESIGN ISSUE
Fencing is damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Emergency light is not working |  | Emergency Light | Emergency Light
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Fiber cables is not properly routed on tower | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Bus bar grounding is missing |  | GROUNDING | GROUNDING
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Outdoor breaker box is rusted |  | OTHERS | OTHERS
Tower grounding leg is missing |  | GROUNDING | GROUNDING
Fencing and rod is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Equipment connected directly to AC |  | DESIGN ISSUE | DESIGN ISSUE
repeater equipments connected directly with A/C |  | DESIGN ISSUE | DESIGN ISSUE
Repeater equipment connected directly with AC |  | DESIGN ISSUE | DESIGN ISSUE
Repeater equipment connected directly with AC |  | DESIGN ISSUE | DESIGN ISSUE
Repeater equipment connected directly with AC |  | DESIGN ISSUE | DESIGN ISSUE
Repeater equipment connected directly with AC |  | DESIGN ISSUE | DESIGN ISSUE
only one PSU is installed and not properly installed |  | DESIGN ISSUE | DESIGN ISSUE
equipment\'s connected directly with AC |  | DESIGN ISSUE | DESIGN ISSUE
MW Dish is not properly installed on scaffolding |  | DESIGN ISSUE | DESIGN ISSUE
Tower paint is required |  | CIVIL_WORK | Paint Job
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Shelter body is rusted |  | CIVIL_WORK | Indoor Shelter
fencing and wire razor is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Pole supportive rods are rusted |  | CIVIL_WORK | Antenna Pole
Pole Antenna mount present |  | CIVIL_WORK | Antenna Pole
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Tower climbing ladder is rusted |  | CIVIL_WORK | Tower
Main gate paint is required |  | CIVIL_WORK | Paint Job
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Cable tray is rusted |  | CIVIL_WORK | Cable Tray
Building outside Spiral ladder is rusted and door is broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
one battery is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Couple of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
One battery is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Bus bar grounding is missing |  | GROUNDING | GROUNDING
Bus bar grounding is missing |  | GROUNDING | GROUNDING
Batteries installation and testing dates is not available | BB installation date tag is not available | BATTERY BACKUP | LABELING
Couple of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
The fence is being damage due to the heavy rocks falling down |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Couples of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Power cable are not properly routed | Main Power Cables not arranged properly | CABLE DRESSING | Power Cable
All batteries are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Main gate paint is required |  | CIVIL_WORK | Paint Job
Site labeling is missing in OSN shelter |  | LABELING | LABELING
Cable is not properly arrange | Cables not arranged properly | CABLE DRESSING | Cables
No proper pathway is available to reach at site |  | OTHERS | OTHERS
Site ID labeling is missing |  | LABELING | LABELING
Couples of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
MAIN grounding cable is missing from bus bars |  | GROUNDING | GROUNDING
Different capacity installed battery backup battery strings | Batteries are in different rating and not Matched | BATTERY BACKUP | BATTERY BACKUP
Couple of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
No safe ladder is available to reach antenna &amp; rru |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cable is not properly arrange | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Main grounding cable is missing from bus bars |  | GROUNDING | GROUNDING
BTS cooling system is not producing cooling |  | DELTA CABINET | AIR_CONDITIONER
BTS cooling system is not producing cooling |  | DELTA CABINET | AIR_CONDITIONER
MAIN grounding cable is not connected with bus bar |  | GROUNDING | GROUNDING
Batteries installation dates is missing | BB installation date tag is not available | BATTERY BACKUP | LABELING
Main grounding cable is missing from bus bar |  | GROUNDING | GROUNDING
No safe ladder to reach antenna &amp; rru |  | DESIGN ISSUE | DESIGN ISSUE
Breaker box lock is damage |  | OTHERS | OTHERS
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Main Grounding cable is missing from bus bar.\r\nRRu grounding cable is missing |  | GROUNDING | GROUNDING
Shelter body has rusted part |  | CIVIL_WORK | Indoor Shelter
Grounding cables is missing |  | GROUNDING | GROUNDING
No proper ladder to reach antenna and rru |  | DESIGN ISSUE | DESIGN ISSUE
All batteries are dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Emergency light is not working |  | Emergency Light | Emergency Light
Different capacity installed battery backup battery strings | Batteries are in different rating and not Matched | BATTERY BACKUP | BATTERY BACKUP
All battery are dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Fiber cable is not secured | Fiber cable are not secured. | CABLE DRESSING | Fiber
Fiber Cable is not routed on cable tray | Fiber cables not arranged properly | CABLE DRESSING | Fiber
All batteries are dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Couples of batteries are dead | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
No proper pathway to reach antenna and rru end |  | DESIGN ISSUE | DESIGN ISSUE
No proper ladder to reach antenna &amp; rru |  | DESIGN ISSUE | DESIGN ISSUE
All batteries are dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
No ladder is available to reach Antenna &amp; rru |  | DESIGN ISSUE | DESIGN ISSUE
Delta door A/c outdoor fan is not working |  | DELTA CABINET | AIR_CONDITIONER
One AC is not working and need to be replaced | One A/C not working need to be replaced | AIR_CONDITIONER | AIR_CONDITIONER
Shelter base has deviation slope |  | CIVIL_WORK | Compound Damage
Not secured / Standing Columns Rusty / Concrete Base Broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
No proper ladder is available to reach antenna &amp; Rru end |  | DESIGN ISSUE | DESIGN ISSUE
All batteries are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Main grounding cable is missing |  | GROUNDING | GROUNDING
Cables is not properly arrange | Cables not arranged properly | CABLE DRESSING | Cables
one battery bank is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Boundary wall have crack issuse |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
V-SAT is installed out of site premises nearby hill top edge |  | DESIGN ISSUE | DESIGN ISSUE
Tower grounding is missing |  | GROUNDING | GROUNDING
Prime CAT DG power cable routing is not proper | Main Power Cables not arranged properly | CABLE DRESSING | Power Cable
4. Need to re route Trunk cable /displaced from ladder | CPRI cables not arranged properly | CABLE DRESSING | CABLE DRESSING
5. In ACDB- Power cable not properly secure | Fiber cable are not secured. | CABLE DRESSING | Fiber
Roxtec not fix properly |  | DESIGN ISSUE | DESIGN ISSUE
External fuel tank pipes are rusty |  | DG ISSUES | DG ISSUES
Tower access ladder foundation is damage |  | DESIGN ISSUE | DESIGN ISSUE
Alarm on MF relay |  | RECTIFIER | RECTIFIER
Access pathway damaged |  | CIVIL_WORK | PATHWAY DAMAGE
One phase was missing inside DB box |  | OTHERS | OTHERS
Grounding is missing |  | GROUNDING | GROUNDING
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Fiber cable displaced from ladder | Fiber cables not arranged properly | CABLE DRESSING | Fiber
power cable is not routed &amp; protected safely |  | CIVIL_WORK | OTHERS
Room have seepage and cracks issuse |  | CIVIL_WORK | Indoor Shelter
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Emergency light is not working |  | Emergency Light | Emergency Light
shelter body is rusty |  | CIVIL_WORK | Indoor Shelter
Site boundary fence is rusty /weak and need to fix properly |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Huawei rectifier battery banks are weak and need to replace | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Boundary wall have cracks |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
BTS cooling system is not working |  | DELTA CABINET | AIR_CONDITIONER
Batteries installation dates is missing | BB installation date tag is not available | BATTERY BACKUP | LABELING
1)Couples of batteries are weak. \r\n2) Couple of batteries are dead. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
BTS cooling system is not working |  | DELTA CABINET | AIR_CONDITIONER
Fiber cable is not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
1)Shelter wall pasted poster need to remove and paint shelter body .\r\n2)Shelter body is rusted |  | CIVIL_WORK | Paint Job
power cable is not routed &amp; protected safely |  | CIVIL_WORK | OTHERS
SITE main fence lock is not working need to maintain |  | OTHERS | OTHERS
OUTDOOR EMERGENCY LIGHT FAULTY |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
Equipment is connected on Ac power |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cables is not secured | Fiber cable are not secured. | CABLE DRESSING | Fiber
BTS cooling system is not working |  | DELTA CABINET | AIR_CONDITIONER
Main grounding is missing from bus bar |  | GROUNDING | GROUNDING
Fiber cables is not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
cables are not properly routed on cable tray | Cables not arranged properly | CABLE DRESSING | Cables
Fiber cables is not secured | Fiber cable are not secured. | CABLE DRESSING | Fiber
All batteries are dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
BTS cooling system is not working |  | DELTA CABINET | AIR_CONDITIONER
Antenna &amp; rru main grounding is missing |  | GROUNDING | GROUNDING
Different capacity installed battery backup battery strings | Batteries are in different rating and not Matched | BATTERY BACKUP | BATTERY BACKUP
All batteries are dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Tower leg foundation cracking need to maintain |  | CIVIL_WORK | Tower
power meter box glass is broken |  | OTHERS | Main DB
battery temp sensor and battery terminals not fastened properly | BB installation date tag is not available | BATTERY BACKUP | LABELING
Battery bank is missing | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Labeling is missing |  | LABELING | LABELING
BTS OD cabinet is not sealed properly |  | DESIGN ISSUE | DESIGN ISSUE
shelter ID light is not working |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
power meter box glass is broken |  | OTHERS | Main DB
cables not fastened properly | Cables not arranged properly | CABLE DRESSING | Cables
site housekeeping in very bad condition and OT related Antena\\\'s are stored inside site premises | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
omentel fence and gate are broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
tower base has cracking |  | CIVIL_WORK | Tower
Batteries installation date is missing | BB installation date tag is not available | BATTERY BACKUP | LABELING
RT poles - Antenna Is not accessible need crane |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cables not arranged properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Couples of battery are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not properly arrange | Fiber cables not arranged properly | CABLE DRESSING | Fiber
No safe ladder to reach Antenna &amp; rru |  | DESIGN ISSUE | DESIGN ISSUE
One battery bank is missing | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Couple of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not secured.\r\n | Fiber cable are not secured. | CABLE DRESSING | Fiber
Couples of batteries are dead | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Couples of batteries are swelled | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
All batteries are dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
No safe ladder is available to reach antenna &amp; RRu |  | DESIGN ISSUE | DESIGN ISSUE
Couples of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Ericsson pbc6500 are available at site |  | DESIGN ISSUE | DESIGN ISSUE
All batteries are dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
BTS cooling system is not producing cooling |  | DELTA CABINET | AIR_CONDITIONER
RT pole supporting rod nut bolts is not properly tight |  | CIVIL_WORK | Antenna Pole
Shelter roof is rusted |  | CIVIL_WORK | Indoor Shelter
O/D cabinet all batteries are dead | O/D cabinet all batteries are dead | BATTERY BACKUP | BATTERY BACKUP
No proper pathway to reach antenna &amp; rru |  | DESIGN ISSUE | DESIGN ISSUE
Delta cabinet filter is missing |  | DELTA CABINET | Delta_Filter
BTS Cooling system is not working |  | DELTA CABINET | AIR_CONDITIONER
All batteries are swelled. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
IF cable is not properly routed | IF cables not arranged properly | CABLE DRESSING | IF
BTS cooling system is not working |  | DELTA CABINET | AIR_CONDITIONER
No safe ladder to reach Antenna end |  | DESIGN ISSUE | DESIGN ISSUE
All batteries are dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
No proper pathway to reach Antenna end |  | DESIGN ISSUE | DESIGN ISSUE
All batteries are dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Delta cabinet cooling system is not producing cooling system |  | DELTA CABINET | AIR_CONDITIONER
No safe ladder is available to reach Ac outdoor units |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cable is not secured | Fiber cable are not secured. | CABLE DRESSING | Fiber
Ericsson PBC6500 is available |  | DESIGN ISSUE | DESIGN ISSUE
Site ID label is not visible |  | LABELING | LABELING
Out door light is not working |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
Rectifier controller display is not working |  | RECTIFIER | RECTIFIER
Batteries installation &amp; testing dates is not available.\r\nBattery bank is missing | BB installation date tag is not available | BATTERY BACKUP | LABELING
Couples of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
All batteries are dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
BTS cooling system is not producing cooling |  | DELTA CABINET | AIR_CONDITIONER
Couples of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Shelter shade are damage |  | CIVIL_WORK | Indoor Shelter
Fiber cable is not secured | Fiber cable are not secured. | CABLE DRESSING | Fiber
Emergency light is not working |  | Emergency Light | Emergency Light
Emergency light is not working |  | Emergency Light | Emergency Light
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Couples of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Battery bank is missing | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Couples of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
All batteries are dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
RDG Power cable is not protected. |  | DG ISSUES | DG ISSUES
Gate need painting and civil action |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
VSAT dish foundation is not as per standard. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
BB is stolen | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Fence is rusted. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
BB is stolen | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
cable tray is rusted |  | CIVIL_WORK | Cable Tray
Housekeeping is required. |  | HOUSEKEEPING | HOUSEKEEPING/Omantel
Tower Paint is required. |  | CIVIL_WORK | Tower
AC is faulty. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Other than Huawei rectifier at site. |  | DESIGN ISSUE | DESIGN ISSUE
AC OD unit safety grill is missing. | AC OD unit safety grill is missing | AIR_CONDITIONER | AIR_CONDITIONER
OD cabinet AC filter is almost choked. |  | DELTA CABINET | Delta_Filter
Other than Huawei rectifier at site. |  | DESIGN ISSUE | DESIGN ISSUE
Fire alarm panel is having fault alarms. |  | FIRE EQUIPMENT | Fire Panel
Need Concrete Base for Vsat Dish |  | DESIGN ISSUE | DESIGN ISSUE
need tower ladder to climb the tower |  | DESIGN ISSUE | DESIGN ISSUE
Pathway is Damaged |  | CIVIL_WORK | PATHWAY DAMAGE
Gate is requiring paint. |  | CIVIL_WORK | Paint Job
Main gate is requiring paint. |  | CIVIL_WORK | Paint Job
Battery backup banks are stolen | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Wire mesh boundary wall need full complete paint |  | CIVIL_WORK | Paint Job
Backup battery banks are stolen | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Boundary wall got damaged and have a critical cracking during rain |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
one PSU got faulty |  | RECTIFIER | RECTIFIER
shelter has rusted part and need complete paint |  | CIVIL_WORK | Paint Job
Tower ladder Base need to repair |  | CIVIL_WORK | Cable Tray
Tower leg grounding is missing |  | GROUNDING | GROUNDING
Shelter bod has visual rust and shelter roof plate need to maintain |  | CIVIL_WORK | Indoor Shelter
site pathway is damaged will be difficult in khareef to reach till the site |  | CIVIL_WORK | PATHWAY DAMAGE
Main DG power cable is not laid underground |  | DG ISSUES | DG ISSUES
Hybrid DG is not working on Auto |  | DG ISSUES | DG ISSUES
door lose and fully rusted needs to be replaced |  | CIVIL_WORK | Indoor Shelter
Fire alarm panel is having fault alarm |  | FIRE EQUIPMENT | Fire Panel Battery
V-Sat cable is not laid properly. | VSAT cables not arranged properly | CABLE DRESSING | CABLE DRESSING
Cabinet 1 AC is faulty. |  | DELTA CABINET | AIR_CONDITIONER
Door locks of both cabinets are faulty. |  | OTHERS | DOOR LOCK
Fiber cables are not protected. | Fiber cable are not secured. | CABLE DRESSING | Fiber
CPRI cable is not routed properly. | CPRI cables not arranged properly | CABLE DRESSING | CABLE DRESSING
Fiber cable are required to rout properly. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Tags on Sec-K &amp; Sec-L rectifiers are missing. |  | LABELING | LABELING
CPRI Cable are not routed are per standard as rolled within / over RRUs. | CPRI cables not arranged properly | CABLE DRESSING | CABLE DRESSING
BB is zero. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
BB is zero. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
CDC system Solar plats are damaged. |  | CIVIL_WORK | OTHERS
Main gate is rusted. |  | CIVIL_WORK | Paint Job
IF cables are not routed properly. | IF cables not arranged properly | CABLE DRESSING | IF
shelter paint is required |  | CIVIL_WORK | Indoor Shelter
site fence/gate is rusted and damaged and easy to access |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site compound below NPT base frame is damaged by rain water |  | CIVIL_WORK | Compound Damage
Battery backup banks are zero | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
site fence/gate is rusted and damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
external tank fuel pipes rusted and need paint |  | DG ISSUES | DG ISSUES
One AC not working need to be replaced | One A/C not working need to be replaced | AIR_CONDITIONER | AIR_CONDITIONER
Site is not secured and easy to access as there is no Boundary wall /Fence |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
RDU towe base frame is rusted and need painting |  | CIVIL_WORK | Paint Job
OD bus bar need greasing |  | OTHERS | OTHERS
Main gate and boundary wire mesh is broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
meter box is rusty and door is broken /tied temporarily by tie wrap | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
boundary Wire mesh is damaged - main gate broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
BB is faulty | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Cable are required to rout properly. | CPRI cables not arranged properly | CABLE DRESSING | CABLE DRESSING
Tower grounding is missing. |  | GROUNDING | GROUNDING
Main gate is missing. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fence is rusted. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Cow located insided PDO camp - There is no boundary wire mesh for site access security |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
all COW tower feeders need to be arranged on priority | COW Tower Ladder Cables Need Arrangement | CABLE DRESSING | CABLE DRESSING
BB is dead. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
BB is stolen | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Lightning rod cable is missing. |  | GROUNDING | GROUNDING
Fiber cable is not secured. | Fiber cable are not secured. | CABLE DRESSING | Fiber
Fiber cables are not secured. | Fiber cable are not secured. | CABLE DRESSING | Fiber
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
1 Rectifier module is faulty. |  | RECTIFIER | RECTIFIER
NARADA weak battery backup string need to replace | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
site went down after AC failure check timely due to zero battery | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Delta cabinet cooling system water leakage need to maintain |  | DELTA CABINET | AIR_CONDITIONER
RDU tower supportive wires are rusted |  | CIVIL_WORK | Tower
hooks not ok |  | OTHERS | OTHERS
BTS Door lock is damage |  | OTHERS | OTHERS
Backup battery strings are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Main gate has critical rust |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Wire mesh is damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
tower access ladder is missing small part |  | CIVIL_WORK | Tower
grounding level under fence concert is damage |  | GROUNDING | GROUNDING
Only one AC is working at site - second AC compressor is faulty | A/C compressor is faulty | AIR_CONDITIONER | Compressor
there is no access ladder to reach to RT antenna |  | DESIGN ISSUE | DESIGN ISSUE
1 AC is faulty. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Meter box door hings are broken. |  | OTHERS | OTHERS
Lightning rod cable is missing. |  | GROUNDING | GROUNDING
1 AC is faulty. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Fiber cables are required to rout properly. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
TN redundant power is missing. |  | DESIGN ISSUE | DESIGN ISSUE
site access pathway is damage and need repairing action |  | CIVIL_WORK | PATHWAY DAMAGE
A/C OD unit has physical damage due to rocks fallen down from hill edge |  | OTHERS | OTHERS
main gate need to maintain and lock is missing | Site main gate padlock is missing | PADLOCK | PADLOCK
Rockslide issue / Site premises is not secured at all as it is located on Hill top - Hill edge Rocks around the site were fell down into the site premises crossing wire mesh fence and caused critical damages in A/C OD Unit / site is in unsafe condition and corrective action need to taken on priority . |  | CIVIL_WORK | CIVIL_WORK
Mini Bus bars are not connected with grounding. |  | GROUNDING | GROUNDING
TN redundant power is missing. |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cables are not secured. | Fiber cable are not secured. | CABLE DRESSING | Fiber
BC is directly connected to CP. |  | DESIGN ISSUE | DESIGN ISSUE
BB is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are required to arrange. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
1 AC is faulty. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Up tower lightening rod is missing |  | GROUNDING | GROUNDING
tower paint is required |  | CIVIL_WORK | Tower
need to paint |  | CIVIL_WORK | Tower
cables need to arrange and cable duct hole is there | CPRI cables not arranged properly | CABLE DRESSING | CABLE DRESSING
operational nod is connected directly with AC |  | DESIGN ISSUE | DESIGN ISSUE
Extra shelter available at site |  | EXTRA MATERIAL | EXTRA MATERIAL
Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
1 ID light is having 1 rod faulty. |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
Air-Cons failure did not report. |  | EXTERNAL ALARM | EXTERNAL ALARM
Vertical ladder foundation is slide off. |  | CIVIL_WORK | Cable Tray
Crack on boundary wall. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
OD cabinet foundation is imbalance. |  | CIVIL_WORK | Foundation
Lightning rod cable is missing. |  | GROUNDING | GROUNDING
BTS cabinet foundation is having crack. |  | CIVIL_WORK | OTHERS
Other than Huawei rectifier at site. |  | DESIGN ISSUE | DESIGN ISSUE
AC is faulty. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
ID Label is required to fix. |  | LABELING | LABELING
Razor wire is damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fire alarm panel is having fault alarm. |  | FIRE EQUIPMENT | Fire Panel
1 ID light is faulty. |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
Intruder is not reported. |  | EXTERNAL ALARM | EXTERNAL ALARM
ID label is required to fix. |  | LABELING | LABELING
Cables arrangement is required. | CPRI cables not arranged properly | CABLE DRESSING | CABLE DRESSING
1 remote is missing. | One A/C remote control is missing | AIR_CONDITIONER | REMOTE MISSING
TN redundant power is missing. |  | DESIGN ISSUE | DESIGN ISSUE
No Proper foundation for fuel tank. |  | DESIGN ISSUE | DESIGN ISSUE
AC automatic control panel is not working. | A/C CONTROL Panel is FAULTY | AIR_CONDITIONER | Control Panel
BB is dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
OD unit is rusted. | One A/C ODU is Rusty | AIR_CONDITIONER | AIR CONTIONER ODU
BB is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Feeder cables arrangement is required. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Fiber cables are required to arrange. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
AC is faulty. |  | DELTA CABINET | AIR_CONDITIONER
Generator is faulty and switched Off - Critical Silver Site |  | DG ISSUES | DG ISSUES
NO SAFE LADDER TO ACCESS ANTEENA |  | DESIGN ISSUE | DESIGN ISSUE
all battery backup banks are weak and need to replace | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
LADDER REQUIRED 5M |  | DESIGN ISSUE | DESIGN ISSUE
Some Unused equips in Room-Old BTS/Rect etc |  | EXTRA MATERIAL | EXTRA MATERIAL
No Proper ladder to Access the Antennas |  | DESIGN ISSUE | DESIGN ISSUE
BB is dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
AC is faulty |  | DELTA CABINET | AIR_CONDITIONER
Site ID label is missing |  | LABELING | LABELING
External alarm not configured(TN have NPU 3C installed and will not support alarm for configuration- design issue) |  | DESIGN ISSUE | DESIGN ISSUE
There is no fence at site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Ericsson rectifier is running at site |  | DESIGN ISSUE | DESIGN ISSUE
need to maintain the painting |  | CIVIL_WORK | Indoor Shelter
Batteries connection not OK |  | OTHERS | OTHERS
1 AC is faulty. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
BB is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fire alarm panel is not working. |  | EXTERNAL ALARM | EXTERNAL ALARM
Door lock is missing. | Site main gate padlock is missing | PADLOCK | Padlock
Roxtec sealing is required. |  | OTHERS | OTHERS
1 Rectifier module is faulty. |  | RECTIFIER | RECTIFIER
Batteries poles are required to clean. | Batteries poles are not Clean/Salted | BATTERY BACKUP | OTHER
Temp sensor is not fixed with batteries. | Temp sensor is not fixed with batteries | BATTERY BACKUP | TEMPERATURE SENSOR
Battery backup banks are stolen from the site | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
2 battery cells are faulty and weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
there is no boundary fence for the site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Repeater cabinet is switched off by Jotun management so site is in disconnected mode |  | OTHERS | OTHERS
Feeder cable are required to rout properly. | Feeder cable are required to route properly | CABLE DRESSING | CABLE DRESSING
Fire alarm panle is faulty. |  | FIRE EQUIPMENT | Fire Panel
Roxtec sealing is required. |  | OTHERS | OTHERS
1 AC is faulty. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Fire alarm box is not working. |  | FIRE EQUIPMENT | Fire Panel
Roxtec sealing is required. |  | OTHERS | OTHERS
Meter box foundation is cracked. |  | CIVIL_WORK | ACDB
Roxtec sealing is required. |  | OTHERS | OTHERS
No proper pathway to access tower. |  | CIVIL_WORK | PATHWAY DAMAGE
Gate lock is missing. | Site main gate padlock is missing | PADLOCK | Padlock
Lightning rod cable is stolen. |  | GROUNDING | GROUNDING
Tower grounding is missing. |  | GROUNDING | GROUNDING
Other than Huawei rectifier at site. |  | DESIGN ISSUE | DESIGN ISSUE
BB is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Poles bolts/ and nuts are rusty and most of pole\'s climbing steps are missing |  | CIVIL_WORK | Antenna pole
Emergency light is not working |  | Emergency Light | Emergency Light
OD grounding bus bar need greasing |  | OTHERS | OTHERS
BTS room lock is faulty but hardly to open | Site main gate padlock is missing | PADLOCK | PADLOCK
wall cracking is there |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
All battery backup banks are fail and need to replace - Silver site | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
power socket is broken |  | CIVIL_WORK | DB
Lightning rod cable is missing. |  | GROUNDING | GROUNDING
Lightning rod cable is stolen. |  | GROUNDING | GROUNDING
Lightning rod cable is stolen. |  | GROUNDING | GROUNDING
Batteries Installation /testing date tag is missing. |  | Labeling | Labeling
Fence is damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Label is missing. |  | LABELING | LABELING
DG cleaning is required. |  | DG ISSUES | DG ISSUES
Earth pit os demolished. |  | GROUNDING | GROUNDING
DG running alarm did not report- checked with FO. |  | DG ISSUES | DG ISSUES
Lightning rod cable is missing. |  | GROUNDING | GROUNDING
Fiber cables are not secured. | Fiber cable are not secured. | CABLE DRESSING | Fiber
Cables arrangement is required. | Cables not arranged properly | CABLE DRESSING | CABLE DRESSING
Other than Huawei rectifier at site. |  | DESIGN ISSUE | DESIGN ISSUE
1 BB is weak. | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
6th Energy devices are no working. |  | OTHERS | OTHERS
MW dishes canvas cover are missing. |  | OTHERS | OTHERS
Pathway is damaged. |  | CIVIL_WORK | PATHWAY DAMAGE
Lightning rod cable is missing. |  | GROUNDING | GROUNDING
Fence gateis damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
tower legs missing grounding - 3 leg grounding not available at all new towers |  | GROUNDING | GROUNDING
emergency light is not working |  | Emergency Light | Emergency Light
Lightning rod cable is missing |  | GROUNDING | GROUNDING
tower painting is not OK |  | CIVIL_WORK | Tower
tower 3 leg grounding is missing - Not available at all new towers |  | GROUNDING | GROUNDING
Fence razor wire broken/rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
RDU tower/nut bolts are rusty and support wires are broken so its need to replace on priority |  | CIVIL_WORK | Tower
Only one AC working due to low capacity portable prime DG | Low capacity prime DG Causing One A/C is not working | AIR_CONDITIONER | AIR_CONDITIONER
there is no fence or boundary wall for this passive repeater |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Labeling is missing |  | LABELING | LABELING
Extra material at site |  | EXTRA MATERIAL | EXTRA MATERIAL
Feeders- Bus bar not grounded/no earth point |  | GROUNDING | GROUNDING
RRU RF connections not properly weather proof |  | OTHERS | OTHERS
cable arrangement required on tower- not proper routed | Tower Ladder Cables Need Arrangement | CABLE DRESSING | Tower
There is no installed fence or boundary wall for this COW |  | COW | Fence / Boundry Wall / Main Gate
feeders not arranged properly along the tower | Tower Ladder Cables Need Arrangement | CABLE DRESSING | Tower
Operational node connected directly with AC |  | DESIGN ISSUE | DESIGN ISSUE
door is jammed due to rust so gate need to maintain |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
fire control panel is faulty |  | FIRE EQUIPMENT | Fire Panel
Site located near sea tower is rusted need paint job |  | CIVIL_WORK | Paint Job
Bolt nuts rusted need paint job |  | CIVIL_WORK | Paint Job
cable tray is rusty |  | CIVIL_WORK | Cable Tray
shelter body is rusted from back side |  | CIVIL_WORK | Indoor Shelter
Access pathway damaged / escalated to whom concern for pathway repairing action |  | CIVIL_WORK | PATHWAY DAMAGE
Access pathway damaged(escalated to concerned team for rectification) |  | CIVIL_WORK | PATHWAY DAMAGE
Ladder base foundation crack |  | CIVIL_WORK | Cable Tray
Wimax battery backup weak | TDD/WiMax Battery Backup is Weak | BATTERY BACKUP | TDD/WiMax
Main gate and fence are rusty- need painting |  | CIVIL_WORK | Paint Job
Main gate and fence are rusty- need painting |  | CIVIL_WORK | Paint Job
wire mesh fence is damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Sector A and Sector B rectifier batteries are bulged so there is no backup | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Antenna bracket is rusted |  | CIVIL_WORK | Antenna pole
site fence or boundary wall is not available /Passive repeater |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fire control panel is faulty |  | FIRE EQUIPMENT | Fire Panel
No proper access pathway to reach at Antenna |  | DESIGN ISSUE | DESIGN ISSUE
VSAT Antenna installed outside fence |  | DESIGN ISSUE | DESIGN ISSUE
Door lock is damaged. |  | OTHERS | OTHERS
OD cabinet BB is mentioned medium. | O/D cabinet all batteries are Weak | BATTERY BACKUP | BATTERY BACKUP
OD cabinet BB is mentioned medium. | O/D cabinet all batteries are Weak | BATTERY BACKUP | BATTERY BACKUP
Fire alarm panel battery is dead. |  | FIRE EQUIPMENT | Fire Panel
Aviation lifht system is not working. | Aviation light system is not working, Need Replace | AVIATION_LIGHT | AVIATION_LIGHT
ID/Emergency lights are faulty. |  | Emergency Light | Emergency Light
Roxtec sealing is required. |  | OTHERS | OTHERS
Fiber cables are not secured. | Fiber cable are not secured. | CABLE DRESSING | Fiber
Batteries are faulty. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Door lock is faulty. |  | OTHERS | OTHERS
some pole\'s nuts are rusty |  | CIVIL_WORK | Antenna pole
grounding and power cables need to arrange along the tower |  | GROUNDING | GROUNDING
Shelter lock is not closing properly | Site main gate padlock is missing | PADLOCK | Padlock
only one A/C is working at site | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
PLC is not working |  | OTHERS | OTHERS
Power cable is not routed and protected properly | Main Power Cables not arranged properly | CABLE DRESSING | Power Cable
one battery cell surface is not clean and weak | BB is weak. | BATTERY BACKUP | OTHER
Fire control panel is showing faulty alarm |  | EXTERNAL ALARM | EXTERNAL ALARM
prim DG and external tank not grounded |  | DG ISSUES | DG ISSUES
Bus bar greasing is required |  | OTHERS | OTHERS
BB installation date tag is not available | BB installation date tag is not available | BATTERY BACKUP | LABELING
Cabinet cleaning is required |  | OTHERS | OTHERS
fire panel is faulty |  | FIRE EQUIPMENT | Fire Panel
Int air con compressor faulty alarm is showing |  | RECTIFIER | RECTIFIER
Internal air con compressor is faulty | A/C compressor is faulty | AIR_CONDITIONER | Compressor
Fuel is stolen from the site |  | OTHERS | OTHERS
Boundary Wire mesh fence is stolen and site is easy to access for everyone |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Boundary wire mesh fence is stolen |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Aviation light system is not installed | Aviation light system need to be installed | AVIATION_LIGHT | AVIATION_LIGHT
there is Ericsson rectifier inside shelter |  | DESIGN ISSUE | DESIGN ISSUE
Monopole fall arrestor vertical line is not proper |  | CIVIL_WORK | Tower
Batteries are faulty (Zero Battery Back-up) | BB installation date tag is not available | BATTERY BACKUP | BATTERY BACKUP
&bull; No smoke sensor installed since site integration for this OD Delta cabinet |  | FIRE EQUIPMENT | Fire Panel
there is no access ladder to RT Antenna |  | DESIGN ISSUE | DESIGN ISSUE
there is no pathway to reach to antenna safely |  | DESIGN ISSUE | DESIGN ISSUE
Cable Tray is Damaged due to rust |  | CIVIL_WORK | Cable Tray
Site Main gate is completely damaged due to rust |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main gate is completely damage due to rust |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Aviation light is Completely damage/need to installed new one | Aviation light system is not working, Need Replace | AVIATION_LIGHT | AVIATION_LIGHT
Aviation light board is faulty | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
OD AC unit is fixed on wall base | OD A/C unit is fixed on wall base | AIR_CONDITIONER | AIR_CONDITIONER
site area is covered by sand |  | CIVIL_WORK | Sand
TN Installed on Hybrid solution and NPU not compatible Alarms not possible to configure |  | DESIGN ISSUE | DESIGN ISSUE
BB is dead. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
AC is faulty. |  | DELTA CABINET | AIR_CONDITIONER
BB is weak / 1 BB is faulty | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
1 AC is faulty. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
No safe ladder to access antennas. |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cables are not secured. | Fiber cable are not secured. | CABLE DRESSING | Fiber
Cables are required to arrange properly. | Cables not arranged properly | CABLE DRESSING | CABLE DRESSING
1 AC is faulty | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Access pathway is damaged. |  | CIVIL_WORK | PATHWAY DAMAGE
V-Sat modem is not fixed properly. |  | DESIGN ISSUE | DESIGN ISSUE
Both aircons are working on manual mode. | Both aircons are working on manual mode | AIR_CONDITIONER | AIR_CONDITIONER
Pathway is required to repair |  | CIVIL_WORK | PATHWAY DAMAGE
Aviation light panel is not working. | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION LIGHT BOARD
Main Gate handle broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main gate concrete pillar damaged and fence wire mesh is damage as well |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fence and gate need painting |  | CIVIL_WORK | Paint Job
MW Antenna cover damaged |  | OTHERS | OTHERS
Access pathway is not reach till the site since site integration ( about 25 m pathway need to maintain ) |  | CIVIL_WORK | PATHWAY DAMAGE
Delta cabinet filter need to clean |  | OTHERS | OTHERS
part of poles are rusty |  | CIVIL_WORK | Antenna Pole
5- No access to the main power meter for site as its in closed area |  | DESIGN ISSUE | DESIGN ISSUE
main gate rods is rusted and damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
there is no main grounding Bus bar for the cow site |  | GROUNDING | GROUNDING
COW Tyre\'sare damaged and need to replace |  | COW | COW
one battery is faulty | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Cabinet AC is faulty. |  | DELTA CABINET | AIR_CONDITIONER
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Batteries are faulty. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
No safe ladder to access antennas. |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
One of rectifiers batteries are faulty. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Couple of cells are faulty. | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Lightning rod cable is missing. |  | GROUNDING | GROUNDING
BB is dead. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
No proper Pathway to access antennas. |  | DESIGN ISSUE | DESIGN ISSUE
Few batteries are faulty. | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
OT tower is rusted |  | CIVIL_WORK | Tower
cable tray has major rust |  | CIVIL_WORK | Cable Tray
Shelter body is rusty |  | CIVIL_WORK | Indoor Shelter
Main gate\'s rods are missing and site access is not secured |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
there is no installed fence at site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
tower is rusty - OT tower |  | CIVIL_WORK | Tower
power meter box is broken - OT is owner |  | CIVIL_WORK | Main DB
Ericsson rectifier is running at site |  | DESIGN ISSUE | DESIGN ISSUE
AC remote battery cells need to replace\\r\\n&bull; No permanent ladder available at site to reach at Antenna / RRU |  | DESIGN ISSUE | DESIGN ISSUE
site leveling is not OK - so soil treatment is required |  | CIVIL_WORK | Compound Damage
extra sun shade pole is available at site |  | EXTRA MATERIAL | EXTRA MATERIAL
This type of Mono-pole tower\'s ladder is not safe to climb by using Double lanyard Hocks so its recommended to install fall arrestor system with life line to climb through and avoid this climbing risk |  | CIVIL_WORK | Tower
battery backup banks are Zero | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Fiber cables not properly routed | Fiber cables not arranged properly | Cable Dressing | Fiber
All under grounding bus bar cover are broken |  | GROUNDING | GROUNDING
one battery bank is missing from this rectifier - according to site Load | One Battery backup string wes stolen | BATTERY BACKUP | BATTERY BACKUP
there is no proper ladder to reach to RT antenna |  | DESIGN ISSUE | DESIGN ISSUE
fiber cables not properly routed and protected | Fiber cables not arranged properly | Cable Dressing | Fiber
one battery cell is fail | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Some minor damage in boundary fence construction |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Cabinet Door cooling system is faulty |  | DELTA CABINET | AIR_CONDITIONER
wire mesh fence having partial damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Some Main gate Rods are damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fence Razor wire broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fiber cables are not secured in both of shelters. | Fiber cable are not secured. | Cable Dressing | Fiber
Bushes are there in front of ladder. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
BB is dead. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Earth pit is demolished. |  | GROUNDING | GROUNDING
Battery cells are weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Gate is damaged . |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Emergency light is faulty. |  | Emergency Light | Emergency Light
Lightning rod cable is missing. |  | GROUNDING | GROUNDING
ATS &amp; AMF panels are not sealed properly. |  | DG ISSUES | DG ISSUES
No proper pathway to site. |  | CIVIL_WORK | PATHWAY DAMAGE
Sand dunes inside the site area. |  | CIVIL_WORK | Sand
IF cable is required to arrange properly. | IF cables not arranged properly | CABLE DRESSING | IF
DG cleaning is required. |  | DG ISSUES | DG ISSUES
DG canopy is rusted. |  | DG ISSUES | DG ISSUES
DG battery is faulty &amp; DG is not working. |  | DG ISSUES | DG ISSUES
Fire alarm panel is faulty. |  | FIRE EQUIPMENT | Fire Panel
DG fuel hoses are not secured. |  | DG ISSUES | DG ISSUES
DG and fuel tank are not grounded. |  | DG ISSUES | DG ISSUES
Pathway is required to repair. |  | CIVIL_WORK | PATHWAY DAMAGE
DG power cable is not secured and routed properly. |  | DG ISSUES | DG ISSUES
IF cable is required to arrange properly. | IF cables not arranged properly | CABLE DRESSING | IF
Temp sensor is required to fix with batteries. | Temp sensor is required to fix with batteries | BATTERY BACKUP | OTHER
Main shelter grounding is missing. |  | GROUNDING | GROUNDING
Main gate lock is missing. | Site main gate padlock is missing | PADLOCK | Padlock
Lightning rod cable is missing. |  | GROUNDING | GROUNDING
V-Sat modem is not fixed properly. |  | DESIGN ISSUE | DESIGN ISSUE
BUC power cable is required to rout properly. | Main Power Cables not arranged properly | Cable Dressing | Power Cable
V-Sat modem is not fixed properly. |  | DESIGN ISSUE | DESIGN ISSUE
V-Sat modem is not fixed properly. |  | DESIGN ISSUE | DESIGN ISSUE
battery back up banks are faulty | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
cooling system is faulty in Both two cabinet |  | DELTA CABINET | AIR_CONDITIONER
Smoke Detector is not installed in both two Delta cabinet |  | DESIGN ISSUE | DESIGN ISSUE
Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Grounding cable is disconnected |  | GROUNDING | GROUNDING
Main gate fence damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Cable tray is totally rusted |  | CIVIL_WORK | Cable Tray
Shelter body is rusted and having damage |  | CIVIL_WORK | Indoor Shelter
Power meter box is damaged and totally rusty | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
Ericsson rectifier is running at site |  | DESIGN ISSUE | DESIGN ISSUE
Cabinet PMU is faulty |  | OTHERS | OTHERS
Cables arrangement action is required ID&amp;OD -Extra dismantled cables need to be removed | Cables not arranged properly | Cable Dressing | CABLE DRESSING
shelter door lock is faulty -Core site |  | OTHERS | Shelter
Emerson rectifier is running at site as well |  | DESIGN ISSUE | DESIGN ISSUE
No pathway to antennas. |  | DESIGN ISSUE | DESIGN ISSUE
Lightning rod cable is missing. |  | GROUNDING | GROUNDING
Intruder did not report- checked with FO. |  | EXTERNAL ALARM | EXTERNAL ALARM
Device is not fixed properly. |  | DESIGN ISSUE | DESIGN ISSUE
TN redundant power is missing. |  | DESIGN ISSUE | DESIGN ISSUE
Only rectifier module is not fixed properly. |  | OTHERS | OTHERS
RDG power cable is not secured. |  | DG ISSUES | DG ISSUES
V-Sate modem is not fixed properly. |  | DESIGN ISSUE | DESIGN ISSUE
Door lock is faulty. |  | OTHERS | OTHERS
Fire alarm panel is having fault. |  | FIRE EQUIPMENT | Fire Panel
DG is turned off due to leakage in fuel returned pipe. |  | DG ISSUES | DG ISSUES
Some of RRUs grounding cables are disconnected. |  | GROUNDING | GROUNDING
Cabinet AC is faulty |  | DELTA CABINET | AIR_CONDITIONER
Fire alarm panel battery is faulty. |  | FIRE EQUIPMENT | Fire Panel
Lightning rod cable is not connected to main grounding. |  | GROUNDING | GROUNDING
Old alarm is there on controller. |  | RECTIFIER | RECTIFIER
DG fuel &amp; Oil filters are not changed since 2017. |  | DG ISSUES | DG ISSUES
DG cleaning is required. |  | DG ISSUES | DG ISSUES
Jumper cables are required to arrange properly. | Cables not arranged properly | Cable Dressing | CABLE DRESSING
PDB panel is rusty |  | CIVIL_WORK | ACDB
Box Glass is broken |  | CIVIL_WORK | Main DB
Fire control panel is not working |  | FIRE EQUIPMENT | Fire Panel
Site housekeeping is require d | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Main grounding connection is missing |  | GROUNDING | GROUNDING
Feeders Earth kit cables are Cut |  | GROUNDING | GROUNDING
lightning rod cable need to tighten properly |  | OTHERS | OTHERS
Meter box door is not closing - box is dirty and glass is missing |  | CIVIL_WORK | Main DB
CB labeling is required |  | LABELING | LABELING
one AC Phase is missing |  | OTHERS | OTHERS
minor damage in wall construction |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fuel leakage is there |  | DG ISSUES | DG ISSUES
Gen is not working on Auto and having alarm |  | DG ISSUES | DG ISSUES
OSN shelter door step is damage |  | CIVIL_WORK | Shelter
tower paint is required |  | CIVIL_WORK | Paint Job
tower foundation is rusted |  | CIVIL_WORK | Tower
cable tray is completely rusted |  | CIVIL_WORK | Cable Tray
Oil leakage from nozzle -Hybrid DG |  | DG ISSUES | DG ISSUES
Power supply cable not protected properly |  | DG ISSUES | DG ISSUES
Boundary Fence is not installed for this RDU site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Prim DG and external tank are not grounded |  | DESIGN ISSUE | DESIGN ISSUE
A/C1 Compressor faulty | A/C compressor is faulty | AIR_CONDITIONER | AIR_CONDITIONER
Site complete grounding system is stolen. |  | GROUNDING | GROUNDING
Lightning rod cable is stolen |  | GROUNDING | GROUNDING
All tower grounding system is stolen |  | GROUNDING | GROUNDING
1 BB is faulty. | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
BTS cabinet door lock is damaged. |  | OTHERS | OTHERS
1 BB is faulty &amp; disconnected. | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
BB are dead. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Delta cabinet AC is faulty. |  | DELTA CABINET | AIR_CONDITIONER
No fence at NPT site. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Cabinet AC is faulty. |  | DELTA CABINET | AIR_CONDITIONER
OSN shelter missing site ID Label |  | LABELING | LABELING
Meter box CB \'s Labeling is missing |  | LABELING | LABELING
Battery banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Tower legs grounding is missing |  | GROUNDING | GROUNDING
Some part of fence is damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Concrete base for cable ladder supporting angle is damaged. |  | CIVIL_WORK | Cable Tray
Temp sensor is missing |  | DESIGN ISSUE | DESIGN ISSUE
Labeling is missing |  | Labeling | Labeling
one battery string is missing | One Battery backup string wes stolen | BATTERY BACKUP | BATTERY BACKUP
CB missing labeling |  | Labeling | Labeling
CB Labeling is missing |  | Labeling | Labeling
RRU poles are rusted |  | CIVIL_WORK | Antenna Pole
There is no installed boundary wall for site access security |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower foundation is not OK - concrete section to be set up under main tower access and wires about to be rusted and need to change |  | CIVIL_WORK | Tower
boundary wall having crack and fence is rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Cabinet door AC is Fail |  | DELTA CABINET | AIR_CONDITIONER
cable tray foundation is cracked |  | CIVIL_WORK | Cable Tray
Site got down while AC power failure alarm checking so site is zero backup batteries and all need to replace | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Delta cabinet Door Air con alarm is showing | Delta cabinet Door Air con alarm is showing | AIR_CONDITIONER | OD CABINET AIR CON
wall corner up head is damage need to maintain |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Door AC is fail |  | DELTA CABINET | AIR_CONDITIONER
There is no installed boundary fence for this RDU Site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site ground leveling is not ok |  | CIVIL_WORK | Compound Damage
Mai n power supply cable is not protected properly | Main Power Cables not arranged properly | Cable Dressing | Power Cable
DG and external tank not grounded |  | DG ISSUES | DG ISSUES
site housekeeping is required /Belong to OT guest site |  | HOUSEKEEPING | HOUSEKEEPING/Omantel
Battery back up of the site is Weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Cabinet AC is faulty. |  | DELTA CABINET | AIR_CONDITIONER
BB is dead. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
OD link grounding is missing |  | GROUNDING | GROUNDING
IF cable arrangement is required | IF cables not arranged properly | CABLE DRESSING | IF
CBs Labeling is missing |  | Labeling | Labeling
Batteries installation date tag is not available |  | Labeling | Labeling
CBs labeling is missing |  | Labeling | Labeling
Batteries of both of cabinets are faulty. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
AC is faulty. |  | DELTA CABINET | AIR_CONDITIONER
Grounding of 1 pole is missing. |  | GROUNDING | GROUNDING
BB is dead. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are required to arrange properly. | Fiber cables not arranged properly | Cable Dressing | Fiber
Emergency light is not working. |  | Emergency Light | Emergency Light
BB is dead. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
RRU pole is required to fix. |  | CIVIL_WORK | Antenna Pole
No enough space to open cabinet door. |  | DESIGN ISSUE | DESIGN ISSUE
Cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Mini busbars for RRU poles are missing. |  | GROUNDING | GROUNDING
Batteries are faulty. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Tower cable arrangement action is required | Tower Ladder Cables Need Arrangement | Cable Dressing | Tower
tower paint is required |  | CIVIL_WORK | Paint Job
Boundary wire mesh and joint points are cut and rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site ground floor is not balanced &amp; OD cabinet verticality is not ok - Civil survey action is required to cross check . |  | CIVIL_WORK | Compound Damage
Tower required to paint |  | CIVIL_WORK | Paint Job
VSAT antenna is damage due to rust |  | OTHERS | OTHERS
damage due to rust |  | CIVIL_WORK | Cable Tray
Tower Bolts rusty |  | CIVIL_WORK | Tower
Shelter body is rusted |  | CIVIL_WORK | Indoor Shelter
Aviation light system is not installed at all | Aviation light system need to be installed | AVIATION_LIGHT | AVIATION_LIGHT
DG and external tank not grounded |  | DG ISSUES | DG ISSUES
External fuel tank is rusty |  | DG ISSUES | DG ISSUES
Boundary wire mesh wall having some rust |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site main gate is fully rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site gate and boundary wall are damage / Site access not secured -OT is a Host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Dismantled shelter with feeder roll still at site premises after Hybrid system implementation with OD cabinet |  | Extra material | Extra material
Boundary wall rods having rust |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
logbook is missing |  | LOG BOOK | LOG BOOK
Box glass is broken but covered by FM |  | OTHERS | Main DB
Site Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
tower ladder is not safe to climb through as ladder is fully rusted |  | CIVIL_WORK | Tower
Shelter body is fully rusty |  | CIVIL_WORK | Indoor Shelter
15M razor wire is damage and Rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
All batteries faulty/drained B.B zero | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Lightning rod cable is stolen |  | GROUNDING | GROUNDING
Temp sensor is missing |  | DESIGN ISSUE | DESIGN ISSUE
Hybrid DG extra tank not grounded and not placed on concrete |  | Extra material | Extra material
All tower legs grounding is missing |  | GROUNDING | GROUNDING
Lightning rod cable is missing. |  | GROUNDING | GROUNDING
Shelter Floor damaged |  | CIVIL_WORK | Indoor Shelter
Site Shelter Floor not leveled and damaged |  | CIVIL_WORK | Foundation
water leakage from shelter roof |  | CIVIL_WORK | Indoor Shelter
A/C2 is faulty | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
no power inside socket |  | OTHERS | OTHERS
grounding cable is cut |  | GROUNDING | GROUNDING
one phase cable is burnt |  | OTHERS | OTHERS
Emergency light is faulty. |  | Emergency Light | Emergency Light
1 AC is faulty. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
BB is dead. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Fiber cables in both of shelters are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Wimax Cabinet AC is faulty. | Wimax Cabinet AC is faulty | AIR_CONDITIONER | AIR_CONDITIONER
Emergency light is faulty. |  | Emergency Light | Emergency Light
Cracks on boundary walls. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Cables arrangement is required. | Cables not arranged properly | Cable Dressing | CABLE DRESSING
1 AC is faulty. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
RDG power cable is not routed properly. |  | DG ISSUES | DG ISSUES
1 Rectifier module port is faulty. |  | RECTIFIER | RECTIFIER
Cracks are there on boundary walls. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Boundary fence is having minor cracking |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Couple of battery cells are faulty. | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
No proper safety ladder to access antenna. |  | DESIGN ISSUE | DESIGN ISSUE
tower foundation is cracked |  | CIVIL_WORK | Tower
Ladder is having some rust |  | CIVIL_WORK | Cable Tray
Box need to clean and seal properly and need labeling as well |  | OTHERS | OTHERS
tower and ladder foundation having crack |  | CIVIL_WORK | Tower
Some extra materials stored inside shelter |  | Extra material | Extra material
DG tank is dirty and need to clean |  | DG ISSUES | DG ISSUES
Labeling is missing |  | Labeling | Labeling
labeling is missing |  | Labeling | Labeling
Cable arrangement is required | Cables not arranged properly | Cable Dressing | CABLE DRESSING
some extra materials need to be removed |  | Extra material | Extra material
Dismental shelter and aircons after hybrid swapped at site |  | Extra material | Extra material
extra materials at site |  | Extra material | Extra material
BB is dead. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
AC is faulty. |  | DELTA CABINET | AIR_CONDITIONER
1 AC is faulty | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
1 Battery cell is faulty. | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Boundary wall having rod rusty and minor foundation cracking |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower grounding system is not connected with main underground system |  | GROUNDING | GROUNDING
NARADA backup batteries are faulty | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
RT poles support foundation cracking |  | CIVIL_WORK | Antenna Pole
Cable tray is having damage part |  | CIVIL_WORK | Cable Tray
ID and OD Fiber cables not protected and routed in proper way | Fiber cables not arranged properly | Cable Dressing | Fiber
One battery cell is faulty | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
External fuel tank with pipes having rust |  | DG ISSUES | DG ISSUES
Glass is broken and inside labeling is missing |  | OTHERS | Main DB
Fiber cable for sector need arrangement | Fiber cables not arranged properly | Cable Dressing | Fiber
TN power redundancy cable is missing |  | DESIGN ISSUE | DESIGN ISSUE
OD Delta cabinet sun shield is broken |  | CIVIL_WORK | OTHERS
Ericsson rectifier is running |  | DESIGN ISSUE | DESIGN ISSUE
DG physical body is rusted |  | DG ISSUES | DG ISSUES
Fence and agate totally damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
dismantled shelter and MW dish still in site premises |  | Extra Material | Extra Material
site subjected to Vandalism |  | OTHERS | OTHERS
Tower is having rust |  | CIVIL_WORK | Tower
there is no fence at site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower Foundation is not OK and tie wires fully rust |  | CIVIL_WORK | Tower
RRU poles rusted |  | CIVIL_WORK | Antenna Pole
MDP is rusted | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
tower main grounding cable is cut |  | GROUNDING | GROUNDING
tower painting is not OK |  | CIVIL_WORK | Paint Job
small bushes need to clean | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Small holes beside tower legs need to maintain |  | CIVIL_WORK | Tower
Gate Wall hock is in loose |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
All battery banks are faulty | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
cooling system is fail |  | DELTA CABINET | AIR_CONDITIONER
ground cable is cut |  | GROUNDING | GROUNDING
2 sectors are located in non accessible location |  | DESIGN ISSUE | DESIGN ISSUE
Small Bushes need to clean | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
there is land fallen area with uncovered ground cables |  | CIVIL_WORK | Compound Damage
Fire panel is not working |  | FIRE EQUIPMENT | Fire Panel
Tower paint is required |  | CIVIL_WORK | Tower
Fiber acable arrangement action is required | Fiber cables not arranged properly | Cable Dressing | Fiber
3. Boundary Wall / Wire Mesh or razor wire are loose/damage/rusted (less than 50%) but secured from intruder |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
VSAT Support is rusty |  | OTHERS | OTHERS
Meter box is having some physical rust | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
1- All 2G and 3G (GSM antenna&rsquo;s) are not grounded. |  | GROUNDING | GROUNDING
2- Sector C antenna earth bus bar missing due to all connected RRU&rsquo;s are not grounded- |  | GROUNDING | GROUNDING
Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
wooden box- mounts- also unused VSAT Dish |  | Extra Material | Extra Material
All site ( Tower - shelter Main gate -- etc ) are so dirty due to weather condition effect |  | CIVIL_WORK | Indoor Shelter
All site physical condition so dirty due to Khareef weather condition |  | CIVIL_WORK | Indoor Shelter
Cable tray Is damage |  | CIVIL_WORK | Cable Tray
Weak Battery Backup of Site (One Battery is Faulty) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
) External alarms is not configured (NPU3C Installed which does not support external alarms) |  | DESIGN ISSUE | DESIGN ISSUE
Extra CAT Rental DG and Fuel tank available at site (CP Connected) |  | Extra Material | Extra Material
Lightning rod cable is missing |  | GROUNDING | GROUNDING
VST Modem is connected directly with AC |  | DESIGN ISSUE | DESIGN ISSUE
One battery bank is faulty | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
aviation light faulty | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
labeling and sealing is required |  | Labeling | Labeling
Site Gate and all site Fence is damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site Foundation is having magor damage due to weather condition |  | CIVIL_WORK | Compound Damage
Toshiba Air-Con #02 has been faulty (PCB KIT) hence 1st aircon is working on manual mode. | A/C PCB kit is faulty | AIR_CONDITIONER | PCB Kit
Site Fence is damage due to last inclement weather in Jabal Akhdar |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
VSAT Dish is covered by Hill fallen stones and need corrective action on priority |  | OTHERS | OTHERS
Shelter Body is rusted |  | CIVIL_WORK | Indoor Shelter
Gate with fence are damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Wire mesh fence is totally damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Prim DG power supply cable is not protected /Routed properly |  | DG ISSUES | DG ISSUES
DG and external tank are not grounded |  | DG ISSUES | DG ISSUES
Lightning rod cable is missing |  | GROUNDING | GROUNDING
Main gate foundation supports are cracked |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Lightning rod cable is missing |  | GROUNDING | GROUNDING
Emerson rectifier is running at site |  | DESIGN ISSUE | DESIGN ISSUE
Pathway repairing action is required |  | CIVIL_WORK | PATHWAY DAMAGE
OD Ericsson TN cabinet cooling system is faulty | Ericsson Outdoor Cabinet AC Faulty | AIR_CONDITIONER | OD CABINET AIR CON
Extra dismantled shelter and tow plastic fuel tanks still available in site premises |  | Extra Material | Extra Material
Tower legs grounding are stolen |  | GROUNDING | GROUNDING
Antenna\'s grounding cable is disconnected |  | GROUNDING | GROUNDING
Extra material left at site (Project team material) |  | Extra Material | Extra Material
Ericsson rectifier is running at site |  | DESIGN ISSUE | DESIGN ISSUE
some rocks fall from the mountain and hit the fence of the site. |  | CIVIL_WORK | CIVIL_WORK
Site Fence is completely damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site Sand removal is required |  | CIVIL_WORK | Sand
Lightning rod cable is missing |  | GROUNDING | GROUNDING
Main Gate Bars has major corrosion and rusty and need civil action.\r\n\r\n |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Battery Banks are stolen- theft case | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Shelter wall has some cracks &amp; Shelter ground is damaged |  | CIVIL_WORK | Indoor Shelter
Air condition is not reachable/Unable to do maintenance |  | DESIGN ISSUE | DESIGN ISSUE
Gate is rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fence is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Grounding is missing |  | GROUNDING | GROUNDING
Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
some leftover materials need to clean |  | Extra Material | Extra Material
All battery backup are faulty | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
fence is cut and having rust |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Delta Cabinet is in very bad physical condition |  | DELTA CABINET | Delta Cabinet
Delta cabinet Fan and cooling system are faulty |  | DELTA CABINET | AIR_CONDITIONER
Gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
extra materials at site |  | Extra Material | Extra Material
Battery backup is zero | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Fiber cables arrangement action is required | Fiber cables not arranged properly | Cable Dressing | Fiber
Cabinet AC is faulty |  | DELTA CABINET | AIR_CONDITIONER
All site battery backup banks are faulty | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Site ground leveling is not OK - Need to maintain |  | CIVIL_WORK | Compound Damage
Lightning rod cable is missing |  | GROUNDING | GROUNDING
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
tower bus bar grounding cables are cut |  | GROUNDING | GROUNDING
DG main power supply cable is not routed and protected properly |  | DG ISSUES | DG ISSUES
DG and external tank not grounded |  | DG ISSUES | DG ISSUES
LOGBOOK IS MISSING |  | LOG BOOK | LOG BOOK
forcibly alarm is appearing on controller |  | OTHERS | OTHERS
Labeling and sealing required \\r\\n |  | Labeling | Labeling
Emergency light is faulty |  | Emergency Light | Emergency Light
one A/C compressor is faulty and both 2 A/C\\\'s on H mode | A/C compressor is faulty | AIR_CONDITIONER | Compressor
some extra material available in Tower compound |  | Extra Material | Extra Material
THERMAL OVERLOAD RELAY FOR AC1 | THERMAL OVERLOAD RELAY FOR AC | AIR_CONDITIONER | AIR_CONDITIONER
Sector A is non accessible as its located on Outside buildings wall |  | DESIGN ISSUE | DESIGN ISSUE
Ladder cable is broken |  | CIVIL_WORK | Cable Tray
All ID cables need to be arranged and routed properly |  | Cable Dressing | CABLE DRESSING
Main grounding cable is cut |  | GROUNDING | GROUNDING
RT site external Spiral and RT antenna ladders are rusted |  | CIVIL_WORK | RT Ladder
There is no safe pathway to Tower on hill -OT is a host |  | CIVIL_WORK | PATHWAY DAMAGE
Cable ladder edge not cover with rubber |  | OTHERS | OTHERS
DG and External tank not grounded |  | DG ISSUES | DG ISSUES
Direct AC PS is there |  | DESIGN ISSUE | DESIGN ISSUE
shelter basement is having cracking |  | CIVIL_WORK | Indoor Shelter
Site ID label is not OK |  | Labeling | Labeling
Telemacanique Logotimer softwer isnt working therefore both aircons are working on manual mode. | A/C LOGOTIMER SW Issue | AIR_CONDITIONER | LOGO TIMER
tower Cable arrangement action is required | Tower Ladder Cables Need Arrangement | Cable Dressing | Tower
there is a dame in site leveling foundation |  | CIVIL_WORK | Compound Damage
soil treatment is required due to old fuel leakage |  | CIVIL_WORK | Compound Damage
DG and external tank are not grounded |  | DG ISSUES | DG ISSUES
Ericsson rectifier is running at the site |  | DESIGN ISSUE | DESIGN ISSUE
Power cable is not protected and routed properly | Main Power Cables not arranged properly | Cable Dressing | Power Cable
Ericsson rectifier is running at the site |  | DESIGN ISSUE | DESIGN ISSUE
DG and external tanks are not grounded |  | DG ISSUES | DG ISSUES
Extra dismantled shelter and semantic Blocks in site premises |  | Extra Material | Extra Material
Showroom is closed by owner -Branch is closed |  | OTHERS | OTHERS
Lightning rod cable is disconnected from down site |  | GROUNDING | GROUNDING
All tower legs grounding is stolen |  | GROUNDING | GROUNDING
Main gate Padlock is missing -Passive Repeater | Site main gate padlock is missing | PADLOCK | Padlock
IBS cabeinet is connected directly with AC |  | DESIGN ISSUE | DESIGN ISSUE
Customer link is powered by AC/DC module only |  | DESIGN ISSUE | DESIGN ISSUE
Site main gate is damaged -OT is a host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
OO-Dismantled Spare(3G RBS- Feeder- Antenna -Sun Shade) are available at site. |  | Extra Material | Extra Material
OT Shared Site Fence is broken. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
1. OO- Dismantled Sun Shade is available at Site. |  | Extra Material | Extra Material
CAT DG fuel tank leakage |  | DG ISSUES | DG ISSUES
DG and external tank not grounded |  | DG ISSUES | DG ISSUES
Extra disconnected Emerson Rectifier available at site. |  | Extra Material | Extra Material
Fiber Cables arrangement action is required | Fiber cables not arranged properly | Cable Dressing | Fiber
Fire panel not installed since shelter/Site deployment |  | DESIGN ISSUE | DESIGN ISSUE
Main gate pillar damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main gate pillar damaged and Main gate have small damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
VSAT dish still not removed from site after migration |  | Extra Material | Extra Material
One battery bank is missing | One Battery backup string wes stolen | BATTERY BACKUP | BATTERY BACKUP
one battery bank is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
main gate is rusty nd need complete painting action |  | CIVIL_WORK | Paint Job
there is no fixed safe ladder to reach to RT antenna |  | DESIGN ISSUE | DESIGN ISSUE
Tower foundation is not OK |  | CIVIL_WORK | Tower
Tower is fully rusty and rigger is not allowed to climb this tower |  | CIVIL_WORK | Tower
Emerson rectifier is running at site |  | DESIGN ISSUE | DESIGN ISSUE
Emerson Rectifier battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site gravel required. |  | CIVIL_WORK | Compound Damage
Box glass is broken |  | OTHERS | Main DB
ID fiber cables not arranged properly | Fiber cables not arranged properly | Cable Dressing | Fiber
Battery backup banks are weak and faulty | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
All battery banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
one Battery bank is stolen | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
only two rectifire modules are on operation mode and there is no running backup |  | DESIGN ISSUE | DESIGN ISSUE
(Hanging Rod damage)/Mono Pole tower |  | CIVIL_WORK | Tower
one Battery cell is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra mount at site premises |  | Extra Material | Extra Material
compound ground has crack |  | CIVIL_WORK | Compound Damage
lighting rod cable is missing |  | GROUNDING | GROUNDING
one of the two shelters is missing site ID Label |  | Labeling | Labeling
Tower foundation is having minor cracking |  | CIVIL_WORK | Tower
Labeling is missing |  | Labeling | Labeling
There is no pathway to the site since integration - pathway repairing is required |  | CIVIL_WORK | PATHWAY DAMAGE
Sand Assembly need to remove from site |  | CIVIL_WORK | Sand
Prim DG AC power cable is not connected properly |  | DG ISSUES | DG ISSUES
Site is zero battery backup due to battery theft case | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Zero BB as banks are theft | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Prim DG cable is not protected Properly |  | DG ISSUES | DG ISSUES
SHELTER Body is having rust |  | CIVIL_WORK | Indoor Shelter
Box door need to maintain - glass is broken and need to seal properly |  | OTHERS | Main DB
COW Guy wires need to be fixed properly |  | COW | OTHERS
Site was having High temperature as one A/C compressor is faulty &amp; 2nd one is not producing cooling - Issue escalated to FM timely for swift rectification | A/C compressor is faulty | AIR_CONDITIONER | Compressor
Prim DG main power supply cable is not protected |  | DG ISSUES | DG ISSUES
BTS Room walls are having seepage and need to maintain / Room surface is also damage |  | CIVIL_WORK | Indoor Shelter
shelter leveling is imbalance |  | CIVIL_WORK | Indoor Shelter
Lightning rod cable is missing |  | GROUNDING | GROUNDING
Tower is rusty and climbing is unsafe |  | CIVIL_WORK | Tower
DG physical body is rusted in out parts |  | DG ISSUES | DG ISSUES
There is no security fence for the site at all |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site need foundation civil maintenance action |  | CIVIL_WORK | Compound Damage
Tower foundation is not OK |  | CIVIL_WORK | Tower
Gate is totally rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra dismantled shelter in site premises |  | Extra Material | Extra Material
Paint is required |  | OTHERS | OTHERS
tower is rusted and need paint |  | CIVIL_WORK | Paint Job
Need to tighten properly |  | OTHERS | OTHERS
Lock is missing | Site main gate padlock is missing | PADLOCK | Padlock
Boundary wall is damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
OD Fiber cables not routed and protected properly | Fiber cables not arranged properly | Cable Dressing | Fiber
AC1 is faulty | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Labeling is missing |  | Labeling | Labeling
housekeeping required (OT is a host) |  | HOUSEKEEPING | HOUSEKEEPING/Omantel
(Battery fuse break &amp; Battery missing) both alarms are reported |  | EXTERNAL ALARM | EXTERNAL ALARM
Rectifire Batteries stolen | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
V-SAT &amp; blocks |  | OTHERS | OTHERS
labeling is missing |  | Labeling | Labeling
AC remote batteries are missing | One A/C remote control Batteries is missing | AIR_CONDITIONER | Remote Batteries
CP labeling is missing |  | Labeling | Labeling
V-SAT node is connecting directly to AC |  | DESIGN ISSUE | DESIGN ISSUE
Shelter main grounding cable is cut |  | GROUNDING | GROUNDING
compound ground not balanced |  | CIVIL_WORK | Compound Damage
Tower not conected to main grounding |  | GROUNDING | GROUNDING
main power supply cable is not protected /fixed properly | Main Power Cables not arranged properly | Cable Dressing | Power Cable
DG &amp; Fule tank are not grounded |  | DG ISSUES | DG ISSUES
fiber cable not protected | Fiber cable are not secured. | Cable Dressing | Fiber
lightning rod cable is missing |  | GROUNDING | GROUNDING
Battery back up is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Tower main grounding cable is cut |  | GROUNDING | GROUNDING
extra Poles available inside compound |  | Extra Material | Extra Material
Boundary wall is having seepage and Main gate is required some rust removal and paint |  | CIVIL_WORK | Paint Job
Backup Batteries are faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Extra poles and materials located inside site premises |  | Extra Material | Extra Material
Site fence is totally rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Prim DG is removed from the site but still some related materials located inside premises |  | DG ISSUES | DG ISSUES
Fence gate lock got faulty and it was open | Site main gate padlock is missing | PADLOCK | Padlock
Delta cabinet AC is faulty |  | DELTA CABINET | AIR_CONDITIONER
WIMAX OD cabinet and shelter rectifier Batteries are faulty | TDD/WiMax Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
AC is faulty | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
site main gate rust less than 50% |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
wires mesh cuted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
fiber cable not protected | Fiber cable are not secured. | Cable Dressing | Fiber
2 Battery Banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site main gate damge/rust more than 50%. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
All antenna Poles are missing grounding cables |  | GROUNDING | GROUNDING
WIFI Max cabinet door is blocking pass to inside room |  | DESIGN ISSUE | DESIGN ISSUE
RT ladder need to be fixed properly from upper end point |  | CIVIL_WORK | RT Ladder
Fiber cables need to protected and routed properly | Fiber cables not arranged properly | Cable Dressing | Fiber
BTS Room is having seepage on walls |  | CIVIL_WORK | Indoor Shelter
OD unit not reachable for maintenance |  | DESIGN ISSUE | DESIGN ISSUE
Delta filter is dirty and need to replace |  | DELTA CABINET | Delta_Filter
Delte cabinet hand lock is damage |  | DELTA CABINET | DOOR LOCK
delta cabinet smoke sensor is broken |  | DELTA CABINET | Sensor
site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Tower bus bar cable is cut |  | GROUNDING | GROUNDING
Power meter box is damage | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
HW fault and some other alarms are showing on rectifier controller r |  | DELTA CABINET | RECTIFIER
All battery backup banks are faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
minor damage is there and dismantles breaker is inside panel |  | OTHERS | OTHERS
one earth cable is disconnected inside cabinet |  | GROUNDING | GROUNDING
cooling system is faulty |  | DELTA CABINET | AIR_CONDITIONER
Delta cabinets locks are damage |  | DELTA CABINET | DOOR LOCK
Outside tree branches are extended over site fence |  | OTHERS | OTHERS
Main gate more rusty required full paint. Also some main gate broken (OT Site) |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main gate has rust and need to paint |  | CIVIL_WORK | Paint Job
small bushes need to remove | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
one boundary wall corner cap is fallen and need civil action to maintain |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
NOK-New Outdoor cabinet-ATP Not Offered |  | OTHERS | OTHERS
Site indoor room wall paint affected from seepage. |  | CIVIL_WORK | Indoor Shelter
Antenna pole rusted and construction is cracked |  | CIVIL_WORK | Antenna Pole
Two Batteries are faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Main gate more rusty required full paint |  | CIVIL_WORK | Paint Job
Battery bank 2 cell 1 is faulty | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Main gate wire mesh damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
OT as a host/fence partially damage. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
OT as a host (fence partially damage). |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Antenna grounding cables not available |  | GROUNDING | GROUNDING
there is no access ladder to RT antenna |  | DESIGN ISSUE | DESIGN ISSUE
BB2 &amp;BB3 are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
lightning rod cable is missing |  | GROUNDING | GROUNDING
some Antenna poles cables are cut |  | GROUNDING | GROUNDING
site housekeeping required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
(OT as a host) main gate lock is missing. | Site main gate padlock is missing (Omantel as Host) | PADLOCK | PADLOCK/Omantel
battery backup banks are zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
delta cabinet lock is faulty |  | DELTA CABINET | DOOR LOCK
there is no pathway to the hilly site since integration |  | CIVIL_WORK | PATHWAY DAMAGE
site houskeeping required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
tower need paint |  | CIVIL_WORK | Paint Job
DG is underrated |  | DESIGN ISSUE | DESIGN ISSUE
Shelter is rusty |  | CIVIL_WORK | Indoor Shelter
Site boundary fence is not available -Passive Repeater |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower base foundation damaged |  | CIVIL_WORK | Tower
Earthing bus bar frame is demolished |  | GROUNDING | GROUNDING
pathway is damage need to fix |  | CIVIL_WORK | PATHWAY DAMAGE
battery back up zero. | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Cable tray need to maintain due to Rockslide |  | CIVIL_WORK | Cable Tray
Cable tray need to maintain due to Rockslide |  | CIVIL_WORK | Cable Tray
Boundary wall damage due to Rockslide |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site Foundation is demolished due to Hill rockslide |  | CIVIL_WORK | Foundation
wire mesh &amp; fence are loose |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
ONE DISMANTLE IDU AND ODU Aircon at site |  | Extra Material | Extra Material
Site compound Sand removal action is required |  | CIVIL_WORK | Sand
TN Installed on Hybrid solution and NPU not compatible Alarms not possible to configure\\r\\n |  | DESIGN ISSUE | DESIGN ISSUE
Site main gate is rusty - OT is a host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main gate Pillar foundation is cracked and damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main ACDB base totally damage | Power meter Box and bases completely rusty-Damaged | CIVIL_WORK | ACDB
2 Battery cells are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
2 Battery banks are faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
ODF Fiber cables not routed and protected | Fiber cables not arranged properly | Cable Dressing | Fiber
Extra material down shelter |  | Extra Material | Extra Material
fiber cables not protected | Fiber cables not arranged properly | Cable Dressing | Fiber
shelter door lock is faulty |  | OTHERS | OTHERS
hosekeeping required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
4 Rectifire PSUS are not working |  | RECTIFIER | RECTIFIER
housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Tower base foundation is having major rust |  | CIVIL_WORK | Tower
Main gate is rusted |  | CIVIL_WORK | Indoor Shelter
Main power meter box is completely rusted and damaged | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
Main gate need to paint |  | CIVIL_WORK | Paint Job
there is no site boundary fence |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra materials left on site (Microwave equipment- Extra feeder cables) / Unused devices for unused technologies need to be dismantled |  | Extra Material | Extra Material
main gate Pillar foundation is having crack |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Labeling is missing |  | Labeling | Labeling
battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Gate is rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Tower Grounding bus bar cables are cutting |  | GROUNDING | GROUNDING
High temp alarm is reporting to FO |  | EXTERNAL ALARM | EXTERNAL ALARM
Pathway repairing is required to hill top site |  | CIVIL_WORK | PATHWAY DAMAGE
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Roxtech sealing is required |  | OTHERS | OTHERS
Major housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Shelter door lock is faulty |  | OTHERS | OTHERS
fuel tank cover is missing |  | DG ISSUES | DG ISSUES
grounding is missing |  | GROUNDING | GROUNDING
AC remote battery is missing. | One A/C remote control Batteries is missing | AIR_CONDITIONER | Remote Batteries
{com fail-(Battery missing 1&amp;2) &amp; (Battery fuse break1&amp;2)} these alarms are reporeted on rectifire controller. |  | RECTIFIER | RECTIFIER
battery back up is zero. | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Aviation light board is faulty | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION LIGHT BOARD
Backup batteries are stolen from the site | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Fire control panel is faulty |  | FIRE EQUIPMENT | Fire Panel
OD lighting is not working |  | Illumination Light | Illumination Light
shelter door lock is faulty |  | OTHERS | OTHERS
one A/C is not working | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
2 battery cells are missing at one string / Stolen | One Battery backup string wes stolen | BATTERY BACKUP | BATTERY BACKUP
Site major housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Extra materials ( VSAT Dish &amp; OT materials ) |  | Extra Material | Extra Material
Main power meter box door is damage and box is rusty | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
Labeling and sealing are required |  | Labeling | Labeling
Main gate lock is faulty | Site main gate padlock is missing | PADLOCK | Padlock
Fire control panel is faulty |  | FIRE EQUIPMENT | Fire Panel
extra materials stored under shelter |  | Extra Material | Extra Material
A/C1 is on Off mode | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Lightning rod cable is missing |  | GROUNDING | GROUNDING
site ID yellow label is missing |  | Labeling | Labeling
Main gate need to paint |  | CIVIL_WORK | Paint Job
Rectifier is not fixed properly due to main power cable route |  | OTHERS | OTHERS
Extra materials placed at site |  | Extra Material | Extra Material
COW Body is having visual rust |  | COW | COW
Site major housekeeping is required on priority - Site is having snake | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Shelter body is having visual rust |  | CIVIL_WORK | Indoor Shelter
Meter box door lock is faulty and tighten by tie wrap |  | CIVIL_WORK | ACDB
site /shelter floor leveling is imbalanced and require major civil action |  | CIVIL_WORK | Compound Damage
Tower legs grounding is missing |  | GROUNDING | GROUNDING
Cable tray and tower ladder base foundation are damaged |  | CIVIL_WORK | Cable Tray
shelter door lock is faulty |  | OTHERS | OTHERS
GLASS IS BROKEN AND BOX PAINTED BLACK COLOUR NOT WHITE |  | OTHERS | Main DB
Main gate is rusty and damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower legs grounding disconnected |  | GROUNDING | GROUNDING
shelter door lock is faulty |  | OTHERS | OTHERS
Emerson rectifier is there |  | DESIGN ISSUE | DESIGN ISSUE
BB2 in OD WIMAX cabinet is faulty | TDD/WiMax Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Extra Bracket and feeders are available in site |  | Extra Material | Extra Material
COW tie wires are loosing due to inclement weather - issue escalated timely to COW team for urgent corrective action |  | COW | OTHERS
site ID label is not matched with COW location |  | Labeling | Labeling
Glass is broken and covered by tape instead |  | OTHERS | Main DB
AC SPD Fault alarm |  | OTHERS | OTHERS
Surge protection device is faulty |  | OTHERS | OTHERS
Site Pathway damaged close to wadi area |  | CIVIL_WORK | PATHWAY DAMAGE
Remote battery cells are missing | One A/C remote control Batteries is missing | AIR_CONDITIONER | Remote Batteries
CAT DG power supply cable is not protected properly |  | DG ISSUES | DG ISSUES
DG and external tank are not grounded |  | DG ISSUES | DG ISSUES
Labeling is missing |  | Labeling | Labeling
Site ID Emergency lighting is not working |  | Emergency Light | Emergency Light
Cables need to arrange properly | Cables not arranged properly | Cable Dressing | Cables
A/C thermostat is faulty | A/C thermostat is faulty | AIR_CONDITIONER | Sensor
one cabinet is connected to AC directly |  | DESIGN ISSUE | DESIGN ISSUE
Rectifier1 - Backup batteries are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
one cell poles need to clean | Batteries poles are not Clean/Salted | BATTERY BACKUP | Other
OD cabinet site ID is missing |  | Labeling | Labeling
Power meter box Door lock is faulty |  | OTHERS | OTHERS
Battery backup banks are Zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
small part of fence mesh is cut |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
OD Cabinet AC internal compressor faulty | A/C compressor is faulty | AIR_CONDITIONER | Compressor
Main gate is rusty less than 50% |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
minor housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Hilly site pathway is damaged and need to repair |  | CIVIL_WORK | PATHWAY DAMAGE
Tower cables arrangement action is required | Tower Ladder Cables Need Arrangement | Cable Dressing | Tower
Labeling is missing |  | Labeling | Labeling
RT Site - access way to the roof is not clear and safe |  | DESIGN ISSUE | DESIGN ISSUE
Major housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
A/C1 is not working | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
MDB door is broken and tighten by tie wrap | Power meter Box door hings/fixation required | CIVIL_WORK | ACDB
Meter box glass is broken |  | OTHERS | Main DB
missing labeling |  | Labeling | Labeling
Major housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Lightning rod cable is missing |  | GROUNDING | GROUNDING
TN jumper need proper arrangement |  | Cable Dressing | CABLE DRESSING
Greasing is required |  | OTHERS | OTHERS
Labeling is missing |  | Labeling | Labeling
2 Battery cells are faulty | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Extra dismantled damage MW dish available on tower /Need to check to who its belong |  | Extra Material | Extra Material
under rounding bus bar hole is damage |  | OTHERS | OTHERS
CP door glass broken. |  | OTHERS | Main DB
Fuel level was low 1% - issue escalated timely to 3rd party team for corrective action |  | OTHERS | OTHERS
Site Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
COW Lower supportive guywire need to maintain |  | OTHERS | OTHERS
RRU water proofing is not ok |  | OTHERS | OTHERS
Housekeeping is required and extra small items need to remove out of the room |  | Extra Material | Extra Material
Some Battery Cells are faulty in different stings | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
WIMAX OD Cabinet - alarm cable im MPU is damaged |  | EXTERNAL ALARM | EXTERNAL ALARM
Door not openening due to Energy system very close |  | DESIGN ISSUE | DESIGN ISSUE
Site have bushes and small scrap | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
dismantled MW dish on the tower plus extra materials at site compound |  | Extra Material | Extra Material
site have big and small bushes | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Dismantled Customer link Cabinet inside shilter |  | Extra Material | Extra Material
Lightening surge arrester earthing strip/cable missing |  | GROUNDING | GROUNDING
Label Totally erased |  | Labeling | Labeling
Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Both Grounding busbars need cleaning and greasing near outdoor cabinet |  | OTHERS | OTHERS
Emerson Rectifier install inside shelter |  | DESIGN ISSUE | DESIGN ISSUE
Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Extra Microwave dishes available at site |  | Extra Material | Extra Material
Totally power meter box totally damage (OT as ahost ) | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
Totally power meter box totally damage (OT as ahost ) | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
Outdoor Delta Cabinet foundation unbalanced |  | CIVIL_WORK | Foundation
Main Circit breaker not have label |  | Labeling | Labeling
Labeling is missing |  | Labeling | Labeling
Labeling is missing |  | Labeling | Labeling
OD site - Dist. panel door lock is faulty and door tighten by tie wrap |  | OTHERS | OTHERS
Tower ladder base si not satbel - need to install properly with block |  | CIVIL_WORK | Cable Tray
Earth bar need clean and greasing |  | OTHERS | OTHERS
Tower legs grounding cables are missing |  | GROUNDING | GROUNDING
some rocks fallen down close to the fence and caused some damaged |  | CIVIL_WORK | CIVIL_WORK
some battery cells are weak in different strings | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Tower leg grounding missing |  | GROUNDING | GROUNDING
Tower ladder not fixed on base |  | CIVIL_WORK | Cable Tray
Shelter foundation have crack |  | CIVIL_WORK | Indoor Shelter
Small meter for razor wire are loose |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra dismantled cabinets inside shelter |  | Extra Material | Extra Material
Boundary wall cracking |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
WIMAX cabinet and ID shelter Battery backup banks are faulty | TDD/WiMax Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Shelter boundary fence and tower boundary fence is having some rust |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
up and down housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
extra materials located under shelter |  | Extra Material | Extra Material
some battery cells are weak in different strings | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
One AC not working( compressor faulty ) | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Battery cells are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Vertical cable ladder support damaged |  | CIVIL_WORK | Cable Tray
Emerson Rectifier power ed on at site |  | DESIGN ISSUE | DESIGN ISSUE
not used MW Antenna on site |  | Extra Material | Extra Material
Power meter panel glass broken |  | CIVIL_WORK | Main DB
Emerson Rectifier work at site |  | DESIGN ISSUE | DESIGN ISSUE
Not as standard ID |  | Labeling | Labeling
&bull; Fence gate rusty more than 50% . |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Two omantel MW dish exist at site |  | Extra Material | Extra Material
Very weak batteries performance (need to replace ) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Emerson Dismantled rectifier is at site |  | Extra Material | Extra Material
Battery cells are faulty in different strings and 4th sting is stolen | One Battery backup string wes stolen | BATTERY BACKUP | BATTERY BACKUP
There is no security gate at site (OT is a host ) |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
One of tower grounding cable is cut |  | GROUNDING | GROUNDING
Site battery backup is weak and 2 strings are missing | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fiber cables need to arrange properly | Fiber cables not arranged properly | Cable Dressing | Fiber
Emergency ligting broken |  | Emergency Light | Emergency Light
&bull; Defected batteries and need to replace (weak BB) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
extra materials at site |  | Extra Material | Extra Material
No logbook at site |  | LOG BOOK | LOG BOOK
Site has no fence |  | COW | Fence / Boundry Wall / Main Gate
Too many extra material at site |  | Extra Material | Extra Material
Bateries performance very weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
No Fence at site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
BTS Door need repair |  | DELTA CABINET | Delta Cabinet
CLU Cooling is not working | HUW cabinet Door CLU Faulty | AIR_CONDITIONER | OD CABINET AIR CON
DG Running not patched. |  | DESIGN ISSUE | DESIGN ISSUE
OT Gate has small parts rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
some parts from wire mesh and razor wires broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
One BTS Fan cooling not work | HUW cabinet Door CLU Faulty | AIR_CONDITIONER | OD CABINET AIR CON
Power meter glass is broken |  | CIVIL_WORK | Main DB
main Grounding not connected |  | GROUNDING | GROUNDING
Fuel Tank is rusty |  | DG ISSUES | DG ISSUES
OT as ahost ( Site Gate damaged) |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site logbook is missing |  | LOG BOOK | LOG BOOK
Labeling is missing |  | Labeling | Labeling
Labeling is required |  | Labeling | Labeling
OD light not working |  | Illumination Light | Illumination Light
not labeled |  | Labeling | Labeling
Ericson rectifier running on site |  | DESIGN ISSUE | DESIGN ISSUE
Not patching as no BTS at site |  | DESIGN ISSUE | DESIGN ISSUE
Dismantled 2.8 MW Dish antennas |  | Extra Material | Extra Material
TN 6P need to be dismantled |  | Extra Material | Extra Material
Too much sands covering DG - urgently required to be removed from site |  | CIVIL_WORK | Sand
Too many sands in site fence need civil action to remove it |  | CIVIL_WORK | Sand
Tower is fully rusty -OT is a host |  | CIVIL_WORK | Tower
Pipes need to insolate properly |  | OTHERS | OTHERS
Main gate and fence is fully rusted -OT is a host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra materials stored inside shelter |  | Extra Material | Extra Material
Fiber cables need save by flexible and rearranged | Fiber cables not arranged properly | Cable Dressing | Fiber
Fence need repairing |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra Material in shelter |  | Extra Material | Extra Material
Extra DG kept on site |  | DG ISSUES | DG ISSUES
VSAT Antenna Kept on site |  | Extra Material | Extra Material
Glass not exist |  | OTHERS | Main DB
there is no safe access way to RT Antenna |  | DESIGN ISSUE | DESIGN ISSUE
shelter is rusty |  | CIVIL_WORK | Indoor Shelter
Fence is rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main gate is rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra materials stored inside shelter plus Dismantled VSAT Dish -Antennas and dismantled TN |  | Extra Material | Extra Material
Tower is having some rust and need to clean and paint |  | CIVIL_WORK | Paint Job
Main power meter box is rusty | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
Main gate is fully rusty -OT is a host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower is rusty and need to paint |  | CIVIL_WORK | Paint Job
Shelter body is rusty |  | CIVIL_WORK | Indoor Shelter
RDU tower ladder is broken |  | CIVIL_WORK | Tower
Fuel pipes are rusty |  | DG ISSUES | DG ISSUES
Extra dismantled shelter with VSAT DISH available at site after Hybrid system implementation |  | Extra Material | Extra Material
No Label for Site ID |  | Labeling | Labeling
Sands are too much |  | CIVIL_WORK | Sand
Ericson OD 6200 Rectifier |  | DESIGN ISSUE | DESIGN ISSUE
No pathway for Tower poles |  | DESIGN ISSUE | DESIGN ISSUE
Complete V-SAT Dish and Complete Cabinet |  | Extra Material | Extra Material
OT-only one tower leg connected to earth |  | GROUNDING | GROUNDING
Missing Grounding Bars and Cables |  | GROUNDING | GROUNDING
Emerson Rectifier available |  | DESIGN ISSUE | DESIGN ISSUE
SIte Gate and Fence totally Rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
4- No pathway for site and site is located on hill top |  | CIVIL_WORK | PATHWAY DAMAGE
V-SAT Foundation need to fix |  | CIVIL_WORK | Foundation
Tower Support need to paint |  | CIVIL_WORK | Paint Job
OD lighting not working |  | Illumination Light | Illumination Light
PBC6200 available |  | DESIGN ISSUE | DESIGN ISSUE
Outdoor lights of both shelters are faulty of both shelter |  | Illumination Light | Illumination Light
Missing log book |  | LOG BOOK | LOG BOOK
PBC6500 Available |  | DESIGN ISSUE | DESIGN ISSUE
Extra Material LTE RRU jumpers |  | Extra Material | Extra Material
DG external fuel tank level pipe not visible |  | DG ISSUES | DG ISSUES
Extra Materials/Antennas kept at site |  | Extra Material | Extra Material
Sands assembly inside fence - require removing |  | CIVIL_WORK | Sand
Dismantle shelter including A/C still kept on location |  | Extra Material | Extra Material
Missing Logbook |  | LOG BOOK | LOG BOOK
Too much accumulated sands / urgent action required to remove it |  | CIVIL_WORK | Sand
Dismantle shelter including A/C still kept on location |  | Extra Material | Extra Material
housekeeping required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Lightning rod cable is cut |  | GROUNDING | GROUNDING
Cables required proper routing and under grounding | Cables not arranged properly/Grounded | Cable Dressing | CABLE DRESSING
Fence is cracked at pillar |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site access is not secured OT and there is no lock | Site main gate padlock is missing (Omantel as Host) | PADLOCK | PADLOCK/Omantel
Some feeder Roll and big Antenna poles |  | Extra Material | Extra Material
Lightning rod cable cut (OT as ahost ) |  | GROUNDING | GROUNDING
Shelter base main grounding cable is cut |  | GROUNDING | GROUNDING
Boundary wall have small cracked |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main tower earth bar cables are cut |  | GROUNDING | GROUNDING
site located inside Factory area - There is no fence installed |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Cable tray is rusty and damaged |  | CIVIL_WORK | Cable Tray
Shelter body is rusty |  | CIVIL_WORK | Indoor Shelter
Need sand removal |  | CIVIL_WORK | Sand
Fiber cables arrangement required | Fiber cables not arranged properly | Cable Dressing | Fiber
Main gate is rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Lightning rod cable is missing |  | Grounding | Grounding
Emersson rectifier is running at site |  | DESIGN ISSUE | DESIGN ISSUE
Wire mesh is having some damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site Major housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Major housekeeping is required -OT is a host |  | HOUSEKEEPING | HOUSEKEEPING/Omantel
fiber Arrangement Required | Fiber cables not arranged properly | Cable Dressing | Fiber
monopole tower paint is required |  | CIVIL_WORK | Paint Job
BC CONNECTED ON AC |  | DESIGN ISSUE | DESIGN ISSUE
Main gate rust less than 50% |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fiber Cables not protected properly | Fiber cables not arranged properly | Cable Dressing | Fiber
Site battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
outside tree cover the site boundary wall / need to cut |  | OTHERS | OTHERS
major housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
fibers cables arrangement required. | Fiber cables not arranged properly | Cable Dressing | Fiber
Fibers cables not protected | Fiber cable are not secured. | Cable Dressing | Fiber
(OT is a host)grounding of Tower legs not connected with main grounding. |  | Grounding | Grounding
Tower bases has Cracking. |  | CIVIL_WORK | Tower
Tower bases has Cracking |  | CIVIL_WORK | Tower
main gate lock is missing.(OT is a host) | Site main gate padlock is missing (Omantel as Host) | PADLOCK | PADLOCK/Omantel
Fences Damage more than 50%. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Battery backup banks are fail and need to replace | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
minor housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Lightning rod cable is missing |  | Grounding | Grounding
only one rectifier in operation- other new rectifier rack present but not connected to equipment |  | Extra Material | Extra Material
shelter body is rusty |  | CIVIL_WORK | Indoor Shelter
Meter box lock is damage and door is tighten by tie wrap |  | CIVIL_WORK | ACDB
only one battery string is available at site as 2nd string is missing | One Battery backup string wes stolen | BATTERY BACKUP | BATTERY BACKUP
Monopole tower paint is required |  | CIVIL_WORK | Tower
Meter box glass is broken |  | CIVIL_WORK | Main DB
Palme tree doesn\'t have safe Fall arrestor system for climbing |  | DESIGN ISSUE | DESIGN ISSUE
small bushes are there | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Batteries Installation Date tag is not available |  | Labeling | Labeling
extra small materials under shelter |  | Extra Material | Extra Material
Small bushes need to clean | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Extra materials inside site premises |  | Extra Material | Extra Material
site access is not secured as there is no fence installed |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
fiber cables need to be arranged &amp; dismantled cables need to be removed | Fiber cables not arranged properly | Cable Dressing | Fiber
Extra material in compound V-SAT |  | Extra Material | Extra Material
shelter bases has crack |  | CIVIL_WORK | Indoor Shelter
access is blocked due to sand issue. |  | CIVIL_WORK | Sand
OD MW link grounding cable is disconnected - RT bus bar need greasing and Antenna poles grounding cables are missing |  | OTHERS | OTHERS
grounding cable is disconnected |  | Grounding | Grounding
there is no RT Ladder to reach to RT antenna |  | DESIGN ISSUE | DESIGN ISSUE
OD unit is out of reach for maintenance |  | DESIGN ISSUE | DESIGN ISSUE
Fiber Cables and some of ladder cables need to be arranged in a proper way also combiner is not well installed on the ladder its touching ID AC unit | Cables not arranged properly | Cable Dressing | Cables
Foundation cracking in Both 2 shelters /Civil repairing action |  | CIVIL_WORK | Indoor Shelter
Power - IF - fiber cables need to be arranged in both 2 shelters | IF cables not arranged properly | CABLE DRESSING | IF
Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Roof ceiling is damajed due to Rain Water seepage |  | CIVIL_WORK | Indoor Shelter
Battery backup banks are fail | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
site logbook is missing |  | LOG BOOK | LOG BOOK
Extra material Available(DG-Shelter-Cement etc |  | Extra Material | Extra Material
Cable tray missing |  | CIVIL_WORK | Cable Tray
Site boundary fence is not installed /PDO Site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
there is no fence surrounding the COW |  | COW | Fence / Boundry Wall / Main Gate
COW TYRE RIMS RUSTED |  | COW | COW
SITE ID LABEL NEED TO FIX |  | Labeling | Labeling
POWER DB BOX UNABLE TO OPEN NEED TO REPLACE DB LOCK |  | OTHERS | OTHERS
Cabinet cleaning is required |  | OTHERS | OTHERS
Battery back up is Weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Shelter body is rusty |  | CIVIL_WORK | Indoor Shelter
Huawei and Emerson |  | DESIGN ISSUE | DESIGN ISSUE
Extra materials ( Bracket and bolts ) beside shelter |  | Extra Material | Extra Material
battery back up is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Ericsson cabinet door lock is faulty. |  | OTHERS | OTHERS
Tower painting is required |  | CIVIL_WORK | Tower
Shelter body need full paint |  | CIVIL_WORK | Indoor Shelter
Emerson rectifier is running at site |  | DESIGN ISSUE | DESIGN ISSUE
Tower ladder base not fixed with concrete |  | CIVIL_WORK | Cable Tray
shelter grounding cable is missing |  | Grounding | Grounding
DG canopy rusty |  | DG ISSUES | DG ISSUES
Site Housekeeping is required -OT Site |  | HOUSEKEEPING | HOUSEKEEPING/Omantel
Tower paint is required -OT Site |  | CIVIL_WORK | Tower
Boundary fence is partially damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
DG canopy and external tank are rusty |  | DG ISSUES | DG ISSUES
DG IS not on working auto mode(ATS panel issue) |  | DG ISSUES | DG ISSUES
ATS Panel need to maintain |  | DG ISSUES | DG ISSUES
Main gate damaged -OT Site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
OT is a host/ fences cuted. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fibers Cables not Protected. | Fiber cable are not secured. | Cable Dressing | Fiber
Fiber Cables not Protected. | Fiber cable are not secured. | Cable Dressing | Fiber
access ladder to MW links &amp; poles is missing. |  | DESIGN ISSUE | DESIGN ISSUE
shelter ladder cabels not fixed propely. |  | Cable Dressing | CABLE DRESSING
Fiber cables are not Protected. | Fiber cable are not secured. | Cable Dressing | Fiber
fibers cabels are not protected. | Fiber cable are not secured. | Cable Dressing | Fiber
RT Poles doesn\'t have safe access |  | DESIGN ISSUE | DESIGN ISSUE
Major housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Fiber cables need to be arranged properly | Fiber cables not arranged properly | Cable Dressing | Fiber
Battery cells are weak and need to replace | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
OD MW link grounding cable is missing - some other RT grounding poles missing as well |  | Grounding | Grounding
Site boundary wall is having cracking |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fiber cables need to arrange in both TN &amp; OSN shelter | Fiber cables not arranged properly | Cable Dressing | Fiber
houskeeping reuired | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Extra material in compound osn cabinet. |  | Extra Material | Extra Material
compound groound has 2 big holes. |  | CIVIL_WORK | Compound Damage
fibers cabels arrangement required. | Fiber cables not arranged properly | Cable Dressing | Fiber
CP door is damaged. |  | CIVIL_WORK | ACDB
Battery back up is weak in LTE shelter. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
All fiber cables are not routed and Protected | Fiber cables not arranged properly | Cable Dressing | Fiber
Fiber cables not routed | Fiber cables not arranged properly | Cable Dressing | Fiber
tower bus bar cables cut and Main underground hole is broken |  | Grounding | Grounding
Fiber cables not Protected &amp; routed | Fiber cable are not secured. | Cable Dressing | Fiber
mountain stones nocked the site fence. |  | CIVIL_WORK | OTHERS
there is no access rod to can access site &amp; tower &amp; main gate rust more than 50%. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Cable tray not fixed properly. |  | CIVIL_WORK | Cable Tray
grounding of one shelter base is not connecting to main grounding. |  | Grounding | Grounding
main gate &amp; fences are rust |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
housekeeping required. |  | HOUSEKEEPING | HOUSEKEEPING/Omantel
bussiens customer connect direct to AC. |  | DESIGN ISSUE | DESIGN ISSUE
shelter dismantel |  | Extra Material | Extra Material
Site housekeeping required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Tower bases has crack |  | CIVIL_WORK | Tower
Cabels inside shelter arrangement required &amp; Fiber cabels not Protected | Fiber cables not arranged properly | Cable Dressing | Fiber
fiber cable not routed &amp; protected. | Fiber cables not arranged properly | Cable Dressing | Fiber
Generator is not working on Auto Mode due to ATS contactor Issue |  | DG ISSUES | DG ISSUES
ATS is not working properly |  | DG ISSUES | DG ISSUES
fiber cable not Routed &amp; protected &amp; feeder cabels arrangement required. | Fiber cables not arranged properly | Cable Dressing | Fiber
Site leveling is not ok |  | CIVIL_WORK | Compound Damage
houskeeping required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
most of cabels arrangement required. |  | Cable Dressing | CABLE DRESSING
DG is not working. |  | DG ISSUES | DG ISSUES
ATS damaged. |  | DG ISSUES | DG ISSUES
Fiber cables not Routed &amp; Protected. | Fiber cables not arranged properly | Cable Dressing | Fiber
Battery back up is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Wire Mesh damage. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
B back up is faulty | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Wire Mesh &amp; fence are damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
other vendor rectifier available at site. |  | DESIGN ISSUE | DESIGN ISSUE
fiber Cables not protected | Fiber cable are not secured. | Cable Dressing | Fiber
DG &amp; external tank grounding are missing |  | DG ISSUES | DG ISSUES
Delta Cabinet frame broken |  | DELTA CABINET | Delta Cabinet
Delta DC Aircon Faulty |  | DELTA CABINET | AIR_CONDITIONER
Delta Cabinet Door Damaged |  | DELTA CABINET | DOOR LOCK
One Rect. Module Faulty |  | DELTA CABINET | Rectifier Module
PSC3 Module is Faulty hence all alarms not working |  | DELTA CABINET | Rectifier Module
Weak Battery Backup | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Ericsson OD Rectifier is working at site |  | DESIGN ISSUE | DESIGN ISSUE
base rusted |  | CIVIL_WORK | Tower
wimax cabinet base demage/crack |  | OTHERS | OTHERS
all sectors antenna poles are rusted |  | CIVIL_WORK | Antenna pole
all OD sectors grounding bus bar not greased |  | OTHERS | OTHERS
Boundary wall cracking is observed |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
main gate rust more than 50% |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower Paint is required. |  | CIVIL_WORK | Paint Job
shelter rust less than 50% |  | CIVIL_WORK | Indoor Shelter
other vendor rectifier available at site. |  | DESIGN ISSUE | DESIGN ISSUE
Fences &amp; Wires Meshs are rusted more than 50% &amp; damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
DG is dirty from outside &amp; rusted. |  | DG ISSUES | DG ISSUES
shelter bases has crack. |  | CIVIL_WORK | Indoor Shelter
OD cabel tray is rusted. |  | CIVIL_WORK | Ladder Broken
Tower climbing ladder not fixed properly &amp; not safe. |  | CIVIL_WORK | Tower
shelter is rusted |  | CIVIL_WORK | Indoor Shelter
Tower is rusted more than 50% &amp; OD cable tray is rusted. |  | CIVIL_WORK | Tower
DG Physical body Is rusted. |  | DG ISSUES | DG ISSUES
shelter body is rusted. |  | CIVIL_WORK | Indoor Shelter
lightning rod cable is missing. |  | Grounding | Grounding
DG and its external tank is not grounded. |  | DG ISSUES | DG ISSUES
other vendor rectifier available at site OSN shelter. |  | DESIGN ISSUE | DESIGN ISSUE
RT Ladder is rusty - Some of Pole nuts are rusty |  | CIVIL_WORK | RT Ladder
cable ladder need to fix properly and cble protection and arrangement is required |  | Cable Dressing | CABLE DRESSING
All battery backup banks are faulty and need to replace | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
one of ID light cover is broken and need to change |  | OTHERS | OTHERS
Cables are on ground and need to install additional cable tray on priority |  | CIVIL_WORK | Cable Tray
RT Ladder is rusty and loose so its need to fix for safe climbing on priority |  | CIVIL_WORK | RT Ladder
Fiber cables need to be protected properly inside flexible | Fiber cable are not secured. | Cable Dressing | Fiber
RT spiral ladder is rusty and antenna RT Ladder need to repair |  | CIVIL_WORK | Cable Tray
BTS room seepage |  | CIVIL_WORK | Indoor Shelter
wire mesh connection joints rusty /Observation |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Housekeeping is required - OT is a host |  | HOUSEKEEPING | HOUSEKEEPING/Omantel
DG is not working under installation. |  | DG ISSUES | DG ISSUES
ATS is not working under installation. |  | DG ISSUES | DG ISSUES
Roof top climbing ladder is not safe. |  | CIVIL_WORK | RT Ladder
OT as a Host/ Main gate lock is missing. | Site main gate padlock is missing (Omantel as Host) | PADLOCK | PADLOCK/Omantel
ATS door lock is faulty. |  | DG ISSUES | DG ISSUES
Tower climbing ladder is not fixed properly. |  | CIVIL_WORK | Tower
shelter access ladder not stable on the ground. |  | CIVIL_WORK | OTHERS
OT as a host/Main gate lock is missing- | Site main gate padlock is missing (Omantel as Host) | PADLOCK | PADLOCK/Omantel
other vendor rectifier available at site. |  | DESIGN ISSUE | DESIGN ISSUE
B backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
OT as a Host/ Site access pathway damged more than 50%. |  | CIVIL_WORK | PATHWAY DAMAGE
shelter bases damaged. |  | CIVIL_WORK | Indoor Shelter
Extra material in compound (V-sat). |  | Extra Material | Extra Material
Fiber cabels are not Protected. | Fiber cable are not secured. | Cable Dressing | Fiber
Other vendor rectifier available at site. |  | DESIGN ISSUE | DESIGN ISSUE
damp in boundary wall. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
other vendor rectifier available at site (Emerson rectifire) |  | DESIGN ISSUE | DESIGN ISSUE
DG grounding is missing. |  | DG ISSUES | DG ISSUES
2 Battery cells are faulty. | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Wire Mesh damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower paint is required. |  | CIVIL_WORK | Paint Job
other vendor rectifier available at site. |  | DESIGN ISSUE | DESIGN ISSUE
OT is a host/site housekeeping is required. |  | HOUSEKEEPING | HOUSEKEEPING/Omantel
OT is a host/Extra material inside compound. |  | Extra Material | Extra Material
Emerson rectifier available at site. |  | DESIGN ISSUE | DESIGN ISSUE
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Boundary wall cracked |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Boundary wall cracked |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shelter body is rusty |  | CIVIL_WORK | Indoor Shelter
Site housekeeping is required /OT is a host |  | HOUSEKEEPING | HOUSEKEEPING/Omantel
Boundary wall cracked |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
EXTRA BBS2000 AND BTS AT SITE |  | Extra Material | Extra Material
Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Main gate is not ok - OT is a host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main gate is not OK - OT is a host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Major housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
outdoor cabinet air filter is choaked | Cabinet need to clean and filter need to replace | AIR_CONDITIONER | OD CABINET AIR CON
Major housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Lightning protection cable is stolen |  | Grounding | Grounding
Extra fuel tank is available at site premises |  | DG ISSUES | DG ISSUES
2 Phases have Problem |  | OTHERS | OTHERS
Main gate is rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower painting is required |  | CIVIL_WORK | Tower
small scrapes required to clean |  | Extra Material | Extra Material
big extra materials at site (DG- Tank- ATS) |  | Extra Material | Extra Material
Old Legacy Rectifier available |  | Extra Material | Extra Material
Fiber cable is not protected. | Fiber cable are not secured. | Cable Dressing | Fiber
Bussiens customer is directly connected to AC supply . |  | DESIGN ISSUE | Design Issue
fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Fiber Cable\\\'s are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
fiber Cable is not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
AC2 is not working. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
(AC Compresser is faulty) alarm is active. | A/C compressor is faulty | AIR_CONDITIONER | Compressor
only one AC is working | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
B back up is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fire alarm kit panel is not available at room. |  | FIRE EQUIPMENT | Fire Panel
Door sensor is not available at room |  | OTHERS | Door Sensor
High temp sensor is not available at room. |  | OTHERS | Temperature Sensor
Air con sensor is not available at room. |  | OTHERS | Air Con Sensor
Battery back up is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
(High tem-recifire filer &amp; cooling) alarms cabels are not connecting properly. |  | OTHERS | OTHERS
Main Gate is rusted &amp; damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
RT Ladder steps broken |  | CIVIL_WORK | RT Ladder
Site Battery backup banks are zero | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Site Major Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Logbook is missing |  | LOG BOOK | LOG BOOK
Fiber Cable\'s are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Only one AC is working at the site because of Prim DG capacity and site load | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Fiber cable not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Backup is weak Wimax Cabinet &amp; Battery backup is medium (Rectifier 2). | TDD/WiMax Battery Backup is Weak | BATTERY BACKUP | BATTERY BACKUP
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fiber Cable\'s are not routed &amp; secured. | Fiber cable are not secured. | Cable Dressing | Fiber
There is no safe ladder to can access antennas. |  | DESIGN ISSUE | DESIGN ISSUE
inflink box is not grounded. |  | DESIGN ISSUE | Design Issue
Fiber Cable\'s are not arranged properly &amp; One customer link is not fixed properly- | Fiber Cable | Cable Dressing | CABLE DRESSING
Fiber Cable\'s are not arranged properly. | Fiber cables not arranged properly | Cable Dressing | Fiber
Fiber Cable\'s are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
(B backup is weak Rectifier 1) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site hosuekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
AC 1 is faulty | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Cable\'s arrangement required &amp; Fiber cable is not secured.. | Fiber cable are not secured. | Cable Dressing | Fiber
Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Weak battery backup | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Boundary wall crack |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DG and external tank are not grounded |  | DG ISSUES | DG ISSUES
2- Main Power cable from generator to Main DP is not secured and buried under ground |  | DG ISSUES | DG ISSUES
Fiber Cables are not secured &amp; ODF is fixed in OSN Rack but door not closed properly. | Fiber cable are not secured. | Cable Dressing | Fiber
Site ID label is missing- |  | Labeling | Labeling
B backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Boundary wall has crack. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
node is connected to AC. |  | DESIGN ISSUE | Design Issue
Wire mesh damage. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
No Safe ladder for rooftop access |  | DESIGN ISSUE | DESIGN ISSUE
No Safe ladder for rooftop access |  | DESIGN ISSUE | DESIGN ISSUE
No Safe ladder TO access to rooftop Antenna |  | DESIGN ISSUE | DESIGN ISSUE
Grounding Bus-bar is missing\\not as per standard |  | Grounding | Grounding
Crack on tower leg(OT host site) |  | CIVIL_WORK | Tower
Low fuel in SDG and SDG not starting |  | DG ISSUES | DG ISSUES
Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site Battery backup banks are faulty | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Lightning rod cable is missing. |  | Grounding | Grounding
Other vendor rectifier available at site (Emerson) |  | DESIGN ISSUE | DESIGN ISSUE
site from back side is not safe (There is no fence). |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
main gate angles are rusted and damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower lightning rod cable is missing |  | Grounding | Grounding
Shelter Body is rusted |  | CIVIL_WORK | Indoor Shelter
Lightning rod cable is missing |  | Grounding | Grounding
Site Battery backup banks are faulty | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
BIG BUSHES NEED TO REMOVE | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Housekeeping is required is not clear | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Extra materials ( RRUs &amp; Cables ) at site premises |  | Extra Material | Extra Material
Tower and shelter step have crack |  | CIVIL_WORK | Tower
One AC compressor faulty(AC hand mode) | A/C compressor is faulty | AIR_CONDITIONER | Compressor
Main gate need painting- |  | CIVIL_WORK | Paint Job
Shelter Body is rusted |  | CIVIL_WORK | Indoor Shelter
Gate base concrete is damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shelter level not balanced and step concrete is cracked |  | CIVIL_WORK | Foundation
DG and external tank is not grounded |  | DG ISSUES | DG ISSUES
DG and external tank are not grounded |  | DG ISSUES | DG ISSUES
DG and external tank are not grounded |  | DG ISSUES | DG ISSUES
Seepage is observed in BTS Room inside walls . |  | CIVIL_WORK | Indoor Shelter
cracks is observed inside walls. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
CP labeling is missing. |  | Labeling | Labeling
DB labeling is missing. |  | Labeling | Labeling
Outdoor cabinet cleaning is required. |  | OTHERS | OTHERS
DG cleaning is required. |  | DG ISSUES | DG ISSUES
Extra shelter is required to dismantel. |  | Extra Material | Extra Material
DG and external tank not grounded |  | DG ISSUES | DG ISSUES
DG and external tank are not grounded |  | DG ISSUES | DG ISSUES
There is no ladder on RT to access site Antenna |  | DESIGN ISSUE | DESIGN ISSUE
Emerson Rectifier is available at site |  | DESIGN ISSUE | DESIGN ISSUE
Emerson rectifier battery backup are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Logbook is missing |  | LOG BOOK | LOG BOOK
Pathway repairing action is required |  | CIVIL_WORK | PATHWAY DAMAGE
there is Emerson rectifier at site |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Shelter is located back side villa and Observed access road to the shelter is not safe has too much trees and grass. |  | DESIGN ISSUE | DESIGN ISSUE
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
There is no safe access road to the site and Tower. |  | CIVIL_WORK | PATHWAY DAMAGE
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
1 PSU is faulty. |  | Rectifier | Rectifier
(Rectifier missing) Alarm is active. |  | Rectifier | Rectifier
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Lightning rod cables is missing. |  | Grounding | Grounding
Lightning rod cable is missing. |  | Grounding | Grounding
observed crack in boundary wall. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra materiel in compound. |  | Extra Material | Extra Material
Tower grounding stolen. |  | Grounding | Grounding
Main Gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
one module faulty |  | Rectifier | Rectifier
No permanent ladder to access RRU / antennas |  | DESIGN ISSUE | DESIGN ISSUE
Boundary fence is completely damaged -Site Access is not secured |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shoto batteries Disconnected from System as Hybrid system is activated |  | OTHERS | OTHERS
Power Dis Panel condition is not OK |  | OTHERS | OTHERS
Cabinet frame problem |  | OTHERS | OTHERS
Big extra material in compound. |  | Extra Material | Extra Material
(AC missing) alarm is active. |  | OTHERS | OTHERS
Earth pit cover broken |  | Grounding | Grounding
Site Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DG canopy is having damage |  | DG ISSUES | DG ISSUES
DG and external tank is having rust |  | DG ISSUES | DG ISSUES
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DG and external tank not grounded |  | DG ISSUES | DG ISSUES
Tower grounding is missing |  | GROUNDING | GROUNDING
Extra materials inside BTS room |  | Extra Material | Extra Material
No proper ladder for accessing the Antenna |  | DESIGN ISSUE | DESIGN ISSUE
Site Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Fiber cables are not routed properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Main Gate entrance Basement having some Damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
A/C is faulty | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
AC-2 is faulty. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not routed properly. | Fiber cables not arranged properly | Cable Dressing | Fiber
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
B backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
1 battery backup is weak &amp; other Battery backup is medium. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Cable tray is not fixed properly |  | CIVIL_WORK | Cable Tray
Main grounding to earth pit is damage |  | Grounding | Grounding
OT tower is rusty |  | CIVIL_WORK | Tower
Old shelter still exist |  | Extra Material | Extra Material
Tower lightning rod cable is missing |  | Grounding | Grounding
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
OT is a host/There is no bad lock for tha main gate. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
earth pit maintenance required. |  | Grounding | Grounding
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Lightning rod cable is missing. |  | Grounding | Grounding
Pathway cut due to new road build behind the site- complete pathway required to repair. |  | CIVIL_WORK | PATHWAY DAMAGE
only one A/C is working as A/C1 is on OFF mode due to fan motor issue | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
labeling is missing |  | Labeling | Labeling
tower foundation is not ok -OT tower |  | CIVIL_WORK | Tower
NOK OT shared |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Access ladder to the RT is not safe |  | DESIGN ISSUE | DESIGN ISSUE
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DG fuel tank is empty |  | DG ISSUES | DG ISSUES
Standby DG is not working |  | DG ISSUES | DG ISSUES
Tower paint is not good |  | CIVIL_WORK | Paint Job
WALL PAINTING IS REQUIRED |  | CIVIL_WORK | Paint Job
Sit housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Generator Auto mode switched into stop mode directly while Main power failure check / Issue escalated to DG team |  | DG ISSUES | DG ISSUES
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
glass is broken and covered by tape |  | OTHERS | Main DB
OD MW link grounding cable is missing |  | Grounding | Grounding
1 battery cell is faulty. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
AC-2 is not working Properly. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Battery backup is weak in rectifier-1. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
AC-2 is not working. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Feeder Cables are not fixed properly. | Fiber cables not arranged properly | Cable Dressing | Fiber
Fiber cable is not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
W-max Battery backup is weak | TDD/WiMax Battery Backup is Weak | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not routed and protected. | Fiber cable are not secured. | Cable Dressing | Fiber
Fiber cables are not routed properly. | Fiber cables not arranged properly | Cable Dressing | Fiber
RT Ladder is not fixed properly |  | CIVIL_WORK | RT Ladder
Fiber cables arrangement action is required | Fiber cables not arranged properly | Cable Dressing | Fiber
Site boundary fence is cracked |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
RDU tower wires and lower section are rusted |  | CIVIL_WORK | Tower
RDU section around the shelter is rusted |  | CIVIL_WORK | Tower
OD unit have some rusted parts and power connection cables cover is missing | One A/C ODU is Rusty | AIR_CONDITIONER | AIR CONTIONER ODU
Box is rusted and power cable is not protected |  | OTHERS | Other
WLU09 device is connected to AC |  | DESIGN ISSUE | Design Issue
Fiber cable is not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
LOR POE Box is connected to AC directly |  | DESIGN ISSUE | Design Issue
Site Battery Backup Banks are Zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Housekeeping is required around our shelter | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
small bushes need housekeeping | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
RT Antenna access ladder is rust and its not safe for climbing |  | CIVIL_WORK | RT Ladder
ID Cables arrangement are required - Fiber Cable\'s are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
One Battery bank is weak in Emerson rectifier &amp; 2 Battery backup is medium. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra material inside the shelter. |  | Extra Material | Extra Material
Housekeeping is Required(Major). | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Site main gate not able to close properly. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower paint is required. |  | CIVIL_WORK | Tower
Fiber cables are not routed properly. | Fiber cables not arranged properly | Cable Dressing | Fiber
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Access ladder to the Antennas is not safe. |  | DESIGN ISSUE | DESIGN ISSUE
physical condition of CP box is damaged |  | CIVIL_WORK | Main DB
Main gate &amp; fences are rusted less than 50%- |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
3 battery banks are weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not arranged properly. | Fiber cables not arranged properly | Cable Dressing | Fiber
site Id labeling is missing. |  | Labeling | Labeling
OD Cable\'s are not arranged properly. | OD cable not arranged properly | Cable Dressing | CABLE DRESSING
All fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
AC-1 is on hand mode | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
W-max Battery backup is weak &amp; Rectifier- have (4 B cells are weak)- | TDD/WiMax Battery Backup is Weak | BATTERY BACKUP | BATTERY BACKUP
2 battery cells in Huawei rectifier &amp; Ericsson Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra Ericsson Cabinet exist inside shelter |  | Extra Material | Extra Material
Fence concrete base require civil action |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shelter is rusted and need to paint |  | CIVIL_WORK | Shelter
Main gate and fence are fully damaged and need to replace it on priority |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
access ladder to the antennas is not safe. |  | CIVIL_WORK | RT Ladder
Wire mesh is damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Some big tree require removing | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
New Antenna Materials Existing |  | Extra Material | Extra Material
Main power meter physical condition is not OK |  | CIVIL_WORK | Main DB
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Some ROT Materials exist in shelter |  | Extra Material | Extra Material
Batteries C.B. is faulty |  | OTHERS | Other
1- Extra material inside room related to LULU store as site is located inside equipment room of LULU hypermarket |  | OTHERS | OTHERS
2- Cable tray is fixed by a metal rod as there is no support to it and if this metal rod is removed the tray will fall |  | OTHERS | OTHERS
Main gate need paint |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
HOUSEKEEPING REQUIRED | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
LADDER SUPPORT ROD BASE CRACKED&amp; TOWER BASE CRACKED MINOR |  | CIVIL_WORK | Ladder
Battery cells are missing | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
main power meter box not fixed properly |  | CIVIL_WORK | Main DB
Business customer link is Connected to AC supply. |  | DESIGN ISSUE | Design Issue
Other vendor rectifier available at site. |  | DESIGN ISSUE | DESIGN ISSUE
Other vendor rectifier available at site. |  | DESIGN ISSUE | Design Issue
OT Shared Site and major housekeeping hazard required to clear (mail shared to OT) |  | HOUSEKEEPING | HOUSEKEEPING/Omantel
LTE TDD batteries weak &amp; 2G/3G batteries medium backup | TDD/WiMax Battery Backup is Weak | BATTERY BACKUP | BATTERY BACKUP
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
LTE TDD outdoor cabinet batteries weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Extra materials in site premises ( Ericsson Dismantled Cabinet and MW dish ) |  | Extra Material | Extra Material
OD cable tray base concrete is damage |  | CIVIL_WORK | Ladder
Boundary wall crack |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower Ladder Base is Crack |  | CIVIL_WORK | Tower
Site Gate has Major Rust and also hinges are broken due to rust |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Minor bushes due to khareef- will auto damaged after Khareef season | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
All columns have major rust request replacement |  | CIVIL_WORK | Tower
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
DG Battery is faulty. |  | DG ISSUES | DG ISSUES
AC-2 is on off mode. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
extra materials ( cable ladders ) placed at the site. |  | Extra Material | Extra Material
Cables are not arranged properly on the tower ladder. | Tower Ladder Cables Need Arrangement | Cable Dressing | Tower
inf links are connected to AC Supply directly. |  | DESIGN ISSUE | Design Issue
(There is over load with connected load- so required to install NEW DG that can support 40 KWA) |  | DESIGN ISSUE | Design Issue
site ID label is missing. |  | Labeling | Labeling
Fiber cable is not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
4 cell batteries are faulty &amp; Battery backup is medium. | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
There is no safe ladder to can Access the antennas. |  | DESIGN ISSUE | Design Issue
fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Fiber Cable\'s are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
5 battery cells are faulty &amp; B backup is medium | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Cabinet cleaning is required from outside. |  | OTHERS | Other
Emerson rectifier is at site |  | DESIGN ISSUE | Design Issue
Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
fiber cable is not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
A/C OD unit is out of reach |  | DESIGN ISSUE | Design Issue
Delta cabinet AC is Faulty. |  | DELTA CABINET | AIR_CONDITIONER
Battery backup is Faulty\\disconnected | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
there is No ladder to can access the roof top. |  | DESIGN ISSUE | DESIGN ISSUE
Delta cabinet A\\C is Faulty. |  | DELTA CABINET | AIR_CONDITIONER
Battery backup is faulty. | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
shelter grounding is missing. |  | Grounding | Grounding
AC-2 is faulty | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
there is No safe ladder to can access the Roof top. |  | DESIGN ISSUE | Design Issue
One A\\C is not working | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
there is No safe ladder for rooftop access. |  | DESIGN ISSUE | Design Issue
Site path way is damage |  | CIVIL_WORK | PATHWAY DAMAGE
Battery Backup is faulty. | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Fence having minor damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Delta cabinet cleaning is required. |  | OTHERS | Other
There is to much sand inside compound. |  | CIVIL_WORK | Sand
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
5 battery cells are faulty &amp; Battery backup is medium/observation. | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Battery bank 2 is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
fiber cable is not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Ericsson Battery backup is weak &amp; Huawei Battery backup is medium/observation. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Observed big hole in fence. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
observed- water leakage inside the walls of the room. |  | CIVIL_WORK | Shelter
3 Battery cells are faulty &amp; Battery backup is medium/observation. | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Mains PH L2 failure) alarm is reported to Rectifier controller. |  | Rectifier | Rectifier
Battery bank 1 is missing. | One Battery backup string wes stolen | BATTERY BACKUP | BATTERY BACKUP
Main gate rust less than 50% |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
one unit available at Room and AC is not producing proper cooling. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
All fences are damaged &amp; rusted. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main gate is rust less than 50%. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Lightning rod cable &amp; tower leg grounding are not connected to the main grounding. |  | Grounding | Grounding
AC filter cleaning is required. |  | OTHERS | Other
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Cabinet cleaning is required. |  | OTHERS | Other
BTS door lock is faulty. |  | DELTA CABINET | DOOR LOCK
Alarm Cables are not connected properly. |  | DELTA CABINET | External Alarm
OT as host/main gate lock is missing. | Site main gate padlock is missing (Omantel as Host) | PADLOCK | PADLOCK/Omantel
Fence is damaged from the main gate side. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
BTS cabinet cleaning is required. |  | OTHERS | Other
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Shelter\'s Rectifier battery banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fuel level is low |  | DG ISSUES | DG ISSUES
Generator was on stop mode and did not start up due to fuel level Low issue |  | DG ISSUES | DG ISSUES
DG Battery is faulty. |  | DG ISSUES | DG ISSUES
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Lightning rod cable is missing. |  | Grounding | Grounding
DG sensor cable is not fixed properly. |  | DG ISSUES | DG ISSUES
Other vendor rectifier available at site (Ericsson). |  | DESIGN ISSUE | Design Issue
After Swap Site AC Aviaction light not working on DC System | Aviation light system need to be installed | AVIATION_LIGHT | AVIATION_LIGHT
grounding is missing |  | Grounding | Grounding
Fiber cable is not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
DG is on stop mode. |  | DG ISSUES | DG ISSUES
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Mono pole tower painting is required |  | CIVIL_WORK | Tower
Fiber cables arrangement action is required in BTS shelter OSN shelter OD Cable protection flexible i damage | Fiber cable not arranged properly | Cable Dressing | Fiber
some nodes connected directly with AC inside BTS Shelter |  | DESIGN ISSUE | Design Issue
there is no installed ladder to reach to RT antennas |  | DESIGN ISSUE | Design Issue
Main gate need to paint |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Shelter Roof repaired required |  | CIVIL_WORK | Shelter
Outdoor APM Batteries is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
There is no road to can access the site By car. |  | CIVIL_WORK | PATHWAY DAMAGE
(fuel tank &amp; DG) are not grounded. |  | DG ISSUES | DG ISSUES
Site Battery banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DG canopy is having minor rust |  | DG ISSUES | DG ISSUES
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
civil action is required to fix the foundation of ( Main power meter box and fence ) problem s |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Minor housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Fire detection not installed at site |  | DESIGN ISSUE | Design Issue
DG canopy door is faulty and tighten by rope |  | DG ISSUES | DG ISSUES
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Observed big holes down side the boundary wall. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra Material inside the compound(V-Sat dish) |  | Extra Material | Extra Material
Ladder safety hoop damaged |  | CIVIL_WORK | Tower
Ladder and Falling arrestor system are partially damaged |  | CIVIL_WORK | RT Ladder
Main gate damaged and rust more than 50%. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Main gate rusted more than 50%. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Big hole &amp; cracks inside the compound ground. |  | CIVIL_WORK | Compound
Vertical tower ladder base is damaged. |  | CIVIL_WORK | Foundation
mobilized DG and fuel tank |  | DG ISSUES | DG ISSUES
Extra MW Dishes with mounts at site |  | Extra Material | Extra Material
main gate Mesh wires are damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
fiber Cable\'s are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Fiber Cable\'s are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Radio device connected to \&quot;AC\&quot;. |  | DESIGN ISSUE | Design Issue
there is more load on Rectifier \&quot;177A\&quot; need more BB. |  | DESIGN ISSUE | Design Issue
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Alarm not patch and not configure |  | DG ISSUES | DG ISSUES
Switch off Power Bypass |  | DG ISSUES | DG ISSUES
wires mesh are damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
1 battery cell is faulty. | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Fiber Cable\'s are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
wire mesh damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Housekeeping is Required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Some PT Materials are available |  | Extra Material | Extra Material
Major rust in fence pillars |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
External fuel tank is rusty |  | DG ISSUES | DG ISSUES
CLU IS FAULTY | HUW cabinet Door CLU Faulty | AIR_CONDITIONER | OD CABINET AIR CON
door lock is faulty |  | OTHERS | OTHERS
Fiber cables are not secured &amp; cables are not arranged properly. | Fiber cable are not secured. | Cable Dressing | Fiber
Main gate wires mesh are damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Main Gate is Totally Rusted and Damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site access Pathway damage |  | CIVIL_WORK | PATHWAY DAMAGE
DG is not working. |  | DG ISSUES | DG ISSUES
Lightning rod cable is missing. |  | Grounding | Grounding
Fiber Cable\'s are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
2. Extra fiber cable rolled behind the shelter |  | Extra Material | Extra Material
DG completely rusted (Old DG installed) |  | DG ISSUES | DG ISSUES
Earth pit cover broken |  | Grounding | Grounding
There is no access to top mountain antenna\'s |  | DESIGN ISSUE | Design Issue
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
External fuel tank is rusty |  | DG ISSUES | DG ISSUES
Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Need housekeeping | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Sand inside the boundary |  | CIVIL_WORK | Sand
DG is having sand inside and need cleaning service |  | DG ISSUES | DG ISSUES
more then 50% Rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
DG canopy is rusty |  | DG ISSUES | DG ISSUES
Main gate is fully rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shelter body is having major rust |  | CIVIL_WORK | Shelter
Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
House Keeping Required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
OmanTel - Fence damaged and require civil action |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Ericsson rectifier PBC present at site |  | DESIGN ISSUE | Design Issue
Rectifier BB is zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
OD LTE cabinet battery banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
1- V-sat dish and modem are located on hill top and no access pathway since beginning of site integration. |  | DESIGN ISSUE | Design Issue
DG Canopy is rusted and door broken |  | DG ISSUES | DG ISSUES
Project team materials at site both OD and ID |  | Extra Material | Extra Material
need tower paint |  | CIVIL_WORK | Tower
Extra materials ( Shelter with Air con system )at site after Hybrid solution and Swapping |  | Extra Material | Extra Material
DC avation light need to be installed at hybrid site |  | DESIGN ISSUE | Aviation Light
Fence is damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
OD lighting is not working |  | Illumination Light | Illumination Light
RT shelter is having major rust |  | CIVIL_WORK | Shelter
no labeling |  | Labeling | Labeling
power supply cable is not protected | Main Power Cables not arranged properly | Cable Dressing | Power Cable
RT access ladder is rusted and broken and need to replace ASAP |  | CIVIL_WORK | RT Ladder
OD cable arrangement is required | OD cable not arranged properly | Cable Dressing | CABLE DRESSING
some cracking in tower foundation /OT tower |  | CIVIL_WORK | Tower
Cable tray foundation is cracked |  | CIVIL_WORK | Cable Tray
There is no safe ladder to reach to antennas |  | DESIGN ISSUE | Design Issue
batch cord is placed on shelter ground floor |  | Cable Dressing | CABLE DRESSING
Boundary wall is cracked /OT is a host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
extra materials ( MW dish and cables ) at site |  | Extra Material | Extra Material
Power meter is Faulty |  | OTHERS | Other
Site Battery banks are zero and need to replace | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
one side of boundary wall is damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
cabinet handle lock is defected |  | DELTA CABINET | DOOR LOCK
Extra materials at site ( Mounts and wooden banks ) |  | Extra Material | Extra Material
Pathway is damaged but we can go by walk |  | CIVIL_WORK | PATHWAY DAMAGE
Tower Legs grounding is missing |  | Grounding | Grounding
Tower painting is required |  | CIVIL_WORK | Tower
Shelter outside near roxtec cable ladder not properly fixed (Civil) |  | CIVIL_WORK | Cable Tray
AC2 OD compressor is faulty | A/C compressor is faulty | AIR_CONDITIONER | Compressor
Delta Cabinet filters need to change |  | DELTA CABINET | Delta_Filter
Battery cabinet lock is faulty / zero battery cabinet |  | DELTA CABINET | DOOR LOCK
some Antenna grounding cables are missing |  | Grounding | Grounding
Main power meter box door locks broken and door is open / located front of the building on the street |  | OTHERS | Other
All site battery banks are fail /Zero Battery | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Main gate chain lock is damage | Site main gate padlock is missing | PADLOCK | Padlock
Cabinet is used to Store Extra materials( Ericsson cabinets - MW Dishes .--.. etc ) |  | Extra Material | Extra Material
All battery banks are fail /Zero Battery | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Delta cabinet cooling system is faulty and cooling alarm is looped |  | DELTA CABINET | AIR_CONDITIONER
OD Bus bar cables are cut and greasing is required |  | OTHERS | Other
Mount nuts are rusted |  | CIVIL_WORK | Antenna Pole
Site Battery backup is Fail / Zero Backup | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Site battery Backup all are fail /Zero battery | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Cooling system is faulty and delta cabinet filter need to change |  | DELTA CABINET | AIR_CONDITIONER
Site Battery backup is zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
site battery backup is zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Main Bus bar hole is completely closed and it should open to maintain the main grounding |  | DESIGN ISSUE | Design Issue
Big extra mounts and some jumpers available at site |  | Extra Material | Extra Material
Site battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Antenna\'s mount grounding cables are missing and some cables are cut |  | Grounding | Grounding
Delta cabinet door Lock is faulty and handle is damaged |  | DELTA CABINET | DOOR LOCK
3 battery cells are fail | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Wall minor cracking is observed |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shelter body sealing is required / Big visible gap between shelter shields |  | CIVIL_WORK | Shelter
MW dish and one RRU grounding cables are disconnected |  | Grounding | Grounding
There is no Ladder installed to reach to RT antenna\'s |  | DESIGN ISSUE | Design Issue
Site Battery banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
there is no installed ladder to reach to RT antenna |  | DESIGN ISSUE | Design Issue
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
minor Scrap Plus one earth rod available at site |  | Extra Material | Extra Material
One cable is flying and need to arrange |  | Cable Dressing | CABLE DRESSING
One Battery string is fail | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Housekeeping is required / some scraps need to remove | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
OD cables need to arrange /cables are flying PLUS OD eathernet cable between shelter and OD cabinet not arranged properly | OD cable not arranged properly | Cable Dressing | CABLE DRESSING
Power meter box door is damage | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
OD LTE cabinet Battery banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
5 battery cells are faulty. | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Main gate is having rust and foundation need civil action |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
main grounding need to maintain and some main grounding cables disconnected |  | Grounding | Grounding
some extra materials ( cable tray parts ) under the shelter |  | Extra Material | Extra Material
One rectifier battery banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site ground leveling is required close to tower legs |  | OTHERS | Other
CP box glass is broken. |  | OTHERS | Main DB
Wire mesh damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
One Battery bank is weak &amp; other one is medium. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
battery bank 2 is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Fuel tank is not grounded. |  | DG ISSUES | DG ISSUES
Main gate has rust more than 50% |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fences &amp; wire mesh are rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
DG and fuel tank are not grounded. |  | DG ISSUES | DG ISSUES
W-MAX Battery backup is faulty. | TDD/WiMax Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Fences are rusted less than 50%. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Access path way damaged. |  | CIVIL_WORK | PATHWAY DAMAGE
Site Battery backup is weak and battery terminals need to clean | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
wall cracking is observed |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main gate is rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site battery backup banks are weak and need to replace | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Tower painting is required |  | CIVIL_WORK | Tower
part of wire mesh is cut and main gate is having partial rust |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site main gate need to fix as its accessible all the time even its locked |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra materials ( Bracket and box ) available at site |  | Extra Material | Extra Material
Site Battery backup banks are faulty and need to replace | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Site grounding cables are cut and stolen |  | Grounding | Grounding
Lightning rod cable is missing |  | Grounding | Grounding
Only one AC is working at site | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
CP is off and Prime DG is there |  | OTHERS | Other
Main gate need to fix as its accessible even when it is locked |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
wall cracking is observed |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Housekeeping is required /OT is a host | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Shelter foundation is not OK |  | CIVIL_WORK | Indoor Shelter
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site housekeeping is requited -Khareef season | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Fence wire mesh is cut and rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra material inside the compound. |  | Extra Material | Extra Material
Rooftop ladder totally rusty and require urgent civil action |  | CIVIL_WORK | RT Ladder
AC-1 is on hand mode. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
2 Battery bank are weak &amp; 2 Battery bank are medium. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Some Antennas are available |  | Extra Material | Extra Material
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra material Near from the cabinet. |  | Extra Material | Extra Material
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Generator is on stop mode. |  | DG ISSUES | DG ISSUES
Main gate has more than 50% rust |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower paint is required. |  | CIVIL_WORK | Tower
Shelter has more than 50% rust from outside. |  | CIVIL_WORK | Shelter
ODU Of A/CS are rusted. | Both A/C ODU is Rusty | AIR_CONDITIONER | AIR CONTIONER ODU
CP box totally damaged &amp; required to replace it |  | CIVIL_WORK | ACDB
All are fences are rusted. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Wire meshs are damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower paint is required. |  | CIVIL_WORK | Tower
Tower access ladder is rusty where major repair required &amp; ladder base is damaged. |  | CIVIL_WORK | Tower
There is no safe adder to reach to roof top antenna |  | DESIGN ISSUE | Design Issue
DG and eternal fuel tank are not grounded |  | DG ISSUES | DG ISSUES
External fuel tank is rusted |  | DG ISSUES | DG ISSUES
DG is not working / Not accepted yet from DG team |  | DG ISSUES | DG ISSUES
ATS is not working |  | DG ISSUES | DG ISSUES
AC-2 is on off mode. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Cover of A/C ODU is not fixed properly. |  | OTHERS | Other
6 Battery Cells are faulty. | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Compresser is faulty alarm reported on the Rectifier controller | A/C compressor is faulty | AIR_CONDITIONER | Compressor
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
CP box glass is damaged. |  | OTHERS | Main DB
AC PH L2 failure &amp; (Amb HS missing) alarms are reported on Rectifier controller. |  | Rectifier | Rectifier
No Access pathway to the tower till the site On-air |  | CIVIL_WORK | PATHWAY DAMAGE
padlock is missing (Omantel host site) | Site main gate padlock is missing | PADLOCK | Padlock
power meter box Glass is broken |  | OTHERS | Main DB
Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Wall cracking is there |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Wall having some cracking |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
one AC on hand mode and 2nd one off | One A/C is working on manual mode | AIR_CONDITIONER | Hand Mode
No safe ladder to reach antennas |  | DESIGN ISSUE | Design Issue
BTS Room painting is required |  | CIVIL_WORK | Shelter
All site battery backup banks are faulty and need to replace | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
RT ladder Wall support need to fix properly / Unsafe to climb |  | CIVIL_WORK | RT Ladder
OD units pipes isolation is required |  | OTHERS | Other
AC1 is on Hand mode and AC2 is not working | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Batteries are weak and need to replace | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
panel door need to fix properly |  | OTHERS | Other
W-MAX Battery backup is weak. | TDD/WiMax Battery Backup is Weak | BATTERY BACKUP | BATTERY BACKUP
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Cables on the tower ladder are not fixed properly. | Tower Ladder Cables Need Arrangement | Cable Dressing | Tower
Rectifier 1 Battery backup is zero. | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Observed high leakage inside the DG. |  | DG ISSUES | DG ISSUES
Cables on the tower ladder are not fixed properly. | Tower Ladder Cables Need Arrangement | Cable Dressing | Tower
DG and external tank are not grounded |  | DG ISSUES | DG ISSUES
Shelter main grounding cable is missing |  | Grounding | Grounding
No safe climbing steps for Microwave |  | DESIGN ISSUE | Design Issue
AC2 is not working as PCB kit Faulty | A/C PCB kit is faulty | AIR_CONDITIONER | PCB Kit
Main grounding pit holes are not opening to maintain |  | OTHERS | Other
BTS Lock is faulty |  | OTHERS | Door Lock
Lightning rod cable is missing |  | Grounding | Grounding
Tower legs grounding is missing |  | Grounding | Grounding
Site Battery Backup is weak and need to replace | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Huawei outdoor AC Faulty | Delta cabinet Door Air con is not | AIR_CONDITIONER | AIR_CONDITIONER
OD AC units Placed on more than 2m height and difficult to maintain |  | DESIGN ISSUE | Design Issue
Site Battery banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Tower grounding is missing. |  | Grounding | Grounding
BTS door lock is faulty. |  | OTHERS | Other
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Main gate lock is missing. | Site main gate padlock is missing | PADLOCK | Padlock
ladder is not safe to can access the (MW link &amp; RF Antennas ) |  | DESIGN ISSUE | Design Issue
(2 Battery banks are weak &amp; 2 Battery banks are medium). | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery bank 1 is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Wall cracking is there |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Wall Cracking is observed |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
One Battery string is fail and need to replace | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
(Com fail) alarm is reported on the rectifier controller. |  | EXTERNAL ALARM | EXTERNAL ALARM
Cable\'s on the tower ladder are not fixed properly. | Tower Ladder Cables Need Arrangement | Cable Dressing | Tower
CP box glass is missing. |  | OTHERS | Main DB
(Comm fail alarm is reported on the rectifier controller. |  | EXTERNAL ALARM | EXTERNAL ALARM
(communication fail) alarm is reported on the rectifier controller. |  | EXTERNAL ALARM | EXTERNAL ALARM
Other vendor rectifier available at site. |  | DESIGN ISSUE | Design Issue
Log book is missing. |  | LOG BOOK | LOG BOOK
Cable Tray Fallen down and damage |  | CIVIL_WORK | Cable Tray
feeder cable tray missing between tower to RRU since site on-air |  | DESIGN ISSUE | Design Issue
Dismantled Emerson Rectifier is available at shelter |  | Extra Material | Extra Material
Site Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
AC 1 is OFF &amp; AC2 is on HAND MODE | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Site Battery Backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
There is no safe ladder to can Access the RF antennas. |  | DESIGN ISSUE | Design Issue
ODF fiber Cable\'s are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
AC-1 is on off mode. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
CP box glass is broken. |  | OTHERS | Main DB
Fire alarm kit is faulty. |  | FIRE EQUIPMENT | Fire Panel
Shelter door lock is faulty. |  | OTHERS | Shelter
ATS door lock is faulty. |  | DG ISSUES | DG ISSUES
Fiber cables are not secured in both shelters. | Fiber cable are not secured. | Cable Dressing | Fiber
Other vendor rectifier available at site. |  | DESIGN ISSUE | Design Issue
There is no safe ladder to can access the RF antennas. |  | DESIGN ISSUE | Design Issue
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Room door lock is faulty. |  | OTHERS | Shelter
2 battery cells are faulty. | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
OD light &amp; emergency light are faulty. |  | Emergency Light | Emergency Light
Fire alarm kit is faulty. |  | FIRE EQUIPMENT | Fire Panel
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Cables on the tower ladder are not fixed properly. | Tower Ladder Cables Need Arrangement | Cable Dressing | Tower
Shelter door lock is faulty.. |  | OTHERS | Shelter
DG is on stop mode. |  | DG ISSUES | DG ISSUES
(Outdoor TS) alarm is reported on the rectifier controller. |  | Rectifier | Rectifier
Big Extra material inside the Compound. |  | Extra Material | Extra Material
lightning rod cable is missing. |  | Grounding | Grounding
Cables on the tower ladder are not fixed properly. | Tower Ladder Cables Need Arrangement | Cable Dressing | Tower
Lightning rod cables is missing. |  | Grounding | Grounding
Site ID label is missing. |  | Labeling | Labeling
Both A/Cs are on hand mode. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Lightning rod cable is missing. |  | Grounding | Grounding
Cables on the tower ladder are not fixed properly. | Tower Ladder Cables Need Arrangement | Cable Dressing | Tower
Lightning rod cable is missing. |  | Grounding | Grounding
Infilink grounding is missing. |  | DESIGN ISSUE | Design Issue
AC-2 is on off mode. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Shelter door mechanically faulty. |  | OTHERS | Shelter
Both A/Cs are on hand mode. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
CP labeling is missing. |  | Labeling | Labeling
Site housekeeping is required / Belongs to Customer Air con Room |  | Extra Material | Extra Material
batteries are missing | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Shelter OD main bus bar grounding cable is disconnected |  | Grounding | Grounding
There is no safe access ladder to reach to RT antenna poles and even main RT access ladder hand rail is broken |  | DESIGN ISSUE | Design Issue
one battery cell is faulty | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Two battery strings are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
OD MW antenna grounding cable is disconnected |  | Grounding | Grounding
RT grounding cables are disconnected |  | Grounding | Grounding
OD fiber box is damage and need to fix |  | OTHERS | Other
Delta filter need to replace and cabinet need to clean |  | DELTA CABINET | Delta_Filter
All site battery packup banks are faulty and need to replace | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
There is no safe ladder to reach to antenna poles |  | DESIGN ISSUE | Design Issue
site battery backup banks are fail and need to replace | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Many of Antenna Grounding cables are disconnected |  | Grounding | Grounding
Site Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
OD MW link grounding is disconnected and main grounding bus bar need to maintain |  | Grounding | Grounding
Site Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
There is unsafe path on roof toward the Ladder and need to fix on priority |  | DESIGN ISSUE | Design Issue
Extra materials beside the BTS Room |  | Extra Material | Extra Material
RT ladder is rusty |  | CIVIL_WORK | RT Ladder
Partial wall seepage is observed |  | CIVIL_WORK | Shelter
One battery string is faulty | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
site backup batteries are fail | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Roxtech sealing is required. |  | OTHERS | Other
1 Battery cell is faulty. | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Extra matrial inside the compound. |  | Extra Material | Extra Material
V-sat grounding is missing. |  | Grounding | Grounding
Fire alarm kit is faulty. |  | FIRE EQUIPMENT | Fire Panel
Extra rectifier inside the shelter. |  | Extra Material | Extra Material
Lightning rod cable is not fixed properly till the end of the tower. |  | Grounding | Grounding
Roxtech sealing is required. |  | OTHERS | Other
RRU grounding is missing. |  | Grounding | Grounding
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
CP labeling is missing. |  | Labeling | Labeling
Roxtech sealing is required. |  | OTHERS | Other
AC-2 is on off mode. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Other vendor rectifier available at site. |  | DESIGN ISSUE | Design Issue
Rectifier 2 Battery backup is weak &amp; Rectifier 1 Battery backup is medium. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
OD shelter light is faulty. |  | Illumination Light | Illumination Light
Roxtech sealing is required. |  | OTHERS | Other
Site ID label is not fixed. |  | Labeling | Labeling
No safe ladder for W@H |  | DESIGN ISSUE | Design Issue
Old dismantled shelter still at site |  | Extra Material | Extra Material
Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Cable tray is rusted |  | CIVIL_WORK | Cable Tray
PDB BOX is damaged and need to be changed |  | CIVIL_WORK | ACDB
Cabinet cleaning is required |  | OTHERS | Other
Fuel tank not grounded |  | DG ISSUES | DG ISSUES
Dismantled-Shelter with Aircon-MW.ANT-Batteries-Fuel Tank available at site |  | Extra Material | Extra Material
No permanent ladder installed for antenna /RRU access |  | DESIGN ISSUE | Design Issue
Shelter need to paint |  | CIVIL_WORK | Indoor Shelter
Lightning rod cable is cut |  | Grounding | Grounding
Logbook is missing |  | LOG BOOK | LOG BOOK
Prim DG Main power supply cable is not protected |  | DG ISSUES | DG ISSUES
OT is a host - Lock is missing | Site main gate padlock is missing | PADLOCK | Padlock
DG and external tank are not grounded |  | DG ISSUES | DG ISSUES
Remote battery cell not available | One A/C remote control Batteries is missing | AIR_CONDITIONER | Remote Batteries
Logbook not available |  | LOG BOOK | LOG BOOK
Site ID label is missing |  | Labeling | Labeling
Shelter cleaning is required |  | OTHERS | Other
Site Housekeeping | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Dismantled shelter with equipment\'s still available at site after Hybrid Solution |  | Extra Material | Extra Material
tower Painting is required |  | CIVIL_WORK | Tower
tower base is damage |  | CIVIL_WORK | Tower
Cable tray is totally rusted |  | CIVIL_WORK | Cable Tray
Tower ladder is rusted completely /Unsafe to climb |  | CIVIL_WORK | Tower
Gate and fence are damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Some Missing -One PFU card is missing |  | DESIGN ISSUE | Design Issue
Main Gate Don\'t close because sand struck the Main gate |  | CIVIL_WORK | Sand
Cable Tray is totally rusted |  | CIVIL_WORK | Cable Tray
Wire Mesh rusted and damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main gate rusted more than 50%. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
(W-Max Battery backup is weak &amp; there is 2 Battery banks are medium). | TDD/WiMax Battery Backup is Weak | BATTERY BACKUP | BATTERY BACKUP
there is Wire mesh damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Battery backup of 2G Rectifier is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Roxtech sealing is required. |  | OTHERS | Shelter
one AC is working on manual mode | One A/C is working on manual mode | AIR_CONDITIONER | Hand Mode
Main gate lock is faulty. | Site main gate padlock is missing | PADLOCK | Padlock
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Main gate totally rusted. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Tower paint is required/observation. |  | CIVIL_WORK | Tower
Main gate is rusted and need to repair |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Sand Outside Gate and unable to close the gate so sand need to remove |  | CIVIL_WORK | Sand
business customer link is connecting to AC directly. |  | DESIGN ISSUE | Design Issue
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
(Battery missing &amp; Battery Fuse break) Alarms are reported on the rectifier controller. |  | EXTERNAL ALARM | EXTERNAL ALARM
Battery backup is zero. | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
(Battery Fuse 3 break- Battery capacity low- Battery 3 IMB- Battery 2 imb &amp; Battery 1 imb) alarms are reported on the rectifier controller &amp; Door alarm is not reported to FO. |  | EXTERNAL ALARM | EXTERNAL ALARM
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Tower wires are not tied properly. |  | CIVIL_WORK | Tower
Shelter door Mechanically damaged and not Close properly. |  | OTHERS | Other
Site Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
A/C2 is not working | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
A/C1 is not working | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Meter glass is broken |  | OTHERS | Main DB
Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Main gate is broken / OT is a host and issue escalated to them throgh FM |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Extra materials belong to Project Team available at site |  | Extra Material | Extra Material
meter box glass is broken |  | OTHERS | Main DB
Lightning rod cable is missing |  | Grounding | Grounding
Logbook is missing |  | LOG BOOK | LOG BOOK
Dismental Fence and NPT tower at old location after relocation |  | Extra Material | Extra Material
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Power meter box foundation is damaged - its shared with OT power meter box / OT is a host and issue escalated to OT |  | CIVIL_WORK | Foundation
Fence is damage /OT is a host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fiber Cable\'s are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
There is no fixed road to can access the site tower. |  | CIVIL_WORK | PATHWAY DAMAGE
Main gate has rust less thsn 50%. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
There is no safe main gate for the site. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
One AC is faulty | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
BTS Cabinet is not level on the compound ground. |  | CIVIL_WORK | Compound
There is no proper pathway toward RRU Antenna located at hill top |  | DESIGN ISSUE | Designe Issue
main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Other vendor rectifier available inside shelter |  | DESIGN ISSUE | Designe Issue
no proper pathway toward RRU/Antenna (located above hill) |  | DESIGN ISSUE | Designe Issue
OD units physical condition is impacted by cyclone and need to maintain | OD units physical condition bad/Damages | AIR_CONDITIONER | AIR CONTIONER ODU
Site battery banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Other vendor rectifier available at site. |  | DESIGN ISSUE | Designe Issue
Other vendor rectifier available at the shelter |  | DESIGN ISSUE | Designe Issue
3 battery cells are faulty. | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
fiber cables are not secured in (1st-2nd &amp; 3rd) shelter) | Fiber cable are not secured. | Cable Dressing | Fiber
Other vendor rectifier available at the shelter(1st- 2nd &amp; 3rd shelter). |  | DESIGN ISSUE | Designe Issue
Ericsson Rectifier Battery backup is weak. (3rd) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra material inside the compound. |  | Extra Material | Extra Material
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
RT ladder hand rail is rusted and broken so need to repair |  | CIVIL_WORK | RT Ladder
MDB labeling is missing |  | Labeling | Labeling
Site battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
2 battery cells are weak &amp; Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Tower main grounding cable is cut and missing |  | Grounding | Grounding
Lightning rod cable is missing |  | Grounding | Grounding
Delta cabinet filter need to change and cabinet cleaning is required |  | DELTA CABINET | Delta_Filter
Site Battery banks are fail / Site went down timely after Main Failure check | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Delta cabinet Air con is fail |  | DELTA CABINET | AIR_CONDITIONER
Delta cabinet filter need to change and cabinet need cabinet need cleaning |  | DELTA CABINET | Delta_Filter
Delta cabinet door lock is damaged |  | DELTA CABINET | DOOR LOCK
Extra material inside the compound. |  | Extra Material | Extra Material
Wire mesh is damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Many OD grounding cables are cut and missing |  | Grounding | Grounding
Fiber cables need to arrange | Fiber cables not arranged properly | Cable Dressing | Fiber
OD unit front cover is damage | OD unit front cover is damage | AIR_CONDITIONER | AIR CONTIONER ODU
Emerson rectifier is at site |  | DESIGN ISSUE | Designe Issue
APM cabinet batteries are fail |  | BATTERY BACKUP | BATTERY BACKUP
Some OD cables need to arrange properly | OD cable not arranged properly | Cable Dressing | CABLE DRESSING
fiber cables need to arrange properly | Fiber cables not arranged properly | Cable Dressing | Fiber
Main OD Grounding plate of the site is cut |  | Grounding | Grounding
some mounts grounding cables are missing |  | Grounding | Grounding
RT ladder installed in a dangerouse place and need to shift this ladder to safer one |  | CIVIL_WORK | RT Ladder
Fiber cable arrangement action is required | Fiber cables not arranged properly | Cable Dressing | Fiber
BTS Room Seepage and wall cracking need to fix |  | CIVIL_WORK | Shelter
Site Battery Backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Emerson rectifier is running |  | DESIGN ISSUE | Designe Issue
Cisco device connected on AC power |  | DESIGN ISSUE | Designe Issue
SDG and fuel tank rusty |  | DG ISSUES | DG ISSUES
ATS panel hinge broken |  | DG ISSUES | DG ISSUES
Tower grounding broken |  | Grounding | Grounding
SDG fuel tank is empty |  | DG ISSUES | DG ISSUES
Outdoor filter damaged/faulty\r\n |  | DELTA CABINET | Delta_Filter
COUSTMER DEVICE WORKING ON DIRECT AC POWER |  | DESIGN ISSUE | Designe Issue
Main gate is damaged and site is easy to access so gate need to fix on priority |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
No proper path way towards RRU/Antenna end (located above Hill) |  | DESIGN ISSUE | Designe Issue
Site Battery Backup is zero | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
AC power directly given to DCN device (DCN device not active currently) \r\n |  | DESIGN ISSUE | Designe Issue
Fiber cables need to arrange properly | Fiber cables not arranged properly | Cable Dressing | Fiber
Battery backup banks are weak in two shelters /Core Site | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DP door damaged. |  | OTHERS | Other
Wire mesh is damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
CP box glass is missing. |  | OTHERS | Main DB
Tower leg foundation damaged(Omantel host) |  | CIVIL_WORK | Tower
Fiber routing required | Fiber cables not arranged properly | Cable Dressing | Fiber
Shelter level inclined |  | CIVIL_WORK | Shelter
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Extra material(MW dish) |  | Extra Material | Extra Material
Sand inside the site |  | CIVIL_WORK | Sand
light not working |  | Illumination Light | Illumination Light
DG alarm Alarm not patched |  | DG ISSUES | DG ISSUES
Fence stolen from site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower painting is required |  | CIVIL_WORK | Tower
Cable tray is rusted and damage due to rust |  | CIVIL_WORK | Cable Tray
Tower need maintenance as nuts bolts are rusted |  | CIVIL_WORK | Tower
Extra materials at site / Belongs to Project team |  | Extra Material | Extra Material
pathway repairing is required |  | CIVIL_WORK | PATHWAY DAMAGE
4 battery cells are weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
power distribution panel is fully rusted and need to replace | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
Main gate is fully rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
2 battery cell are weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra material inside compound. |  | Extra Material | Extra Material
W-max battery backup is weak. | TDD/WiMax Battery Backup is Weak | BATTERY BACKUP | BATTERY BACKUP
V-Sat device is connecting direct to the AC. |  | DESIGN ISSUE | Designe Issue
Lightning rod cables is missing. |  | Grounding | Grounding
Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fiber cables is not routed properly. | Fiber cables not arranged properly | Cable Dressing | Fiber
Meter box glass is broken |  | OTHERS | Main DB
cable tray is rusted |  | CIVIL_WORK | Cable Tray
Meter box is rusted and door need to fix |  | CIVIL_WORK | ACDB
one battery backup bank is stolen | One Battery backup string wes stolen | BATTERY BACKUP | BATTERY BACKUP
gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
All fences are damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Door need civil action to repair |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
BTS Room seepage and cracking |  | CIVIL_WORK | Indoor Shelter
power meter box glass is broken |  | OTHERS | Main DB
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Other vendor rectifier Available at site. |  | DESIGN ISSUE | Designe Issue
site having major foundation cracking |  | CIVIL_WORK | Foundation
meter box glass is broken |  | OTHERS | Main DB
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Battery bank 2 is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
BTS door lock is faulty. |  | OTHERS | Door Lock
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Rectifier Battery bank is faulty | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Wires mesh are damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
1 battery cell is faulty &amp; 1 Battery bank is medium/observation. | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Other vendor rectifier available at site |  | DESIGN ISSUE | DESIGN ISSUE
7 Battery cells are weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Battery bank 1 is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
6 battery cells are weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
OD fiber box is damaged. | Fiber cables not arranged properly | Cable Dressing | Fiber
ID &amp; OD (Fiber cables are not secured). | Fiber cable are not secured. | Cable Dressing | Fiber
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
W-Max battery backup is weak. | TDD/WiMax Battery Backup is Weak | BATTERY BACKUP | BATTERY BACKUP
cables are not arranged and secured properly. | Fiber cable are not secured. | Cable Dressing | Fiber
Battery label is missing. |  | Labeling | Labeling
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
1 battery cell is faulty. | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
part from the fences is missing. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Cables are not protected- | Cables Secure | Cable Dressing | CABLE DRESSING
Infilink connected to the AC. |  | DESIGN ISSUE | DESIGN ISSUE
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Wires mesh are damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Main gate rusted less than 50%. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
6 battery cells are weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Tower located on the hilltop and there is no road to can access the tower. |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cable is not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
(Battery bank \&quot;1\&quot;) is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site Battery banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
housekeeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
fiber cables are not Secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
OD &amp; ID (fiber cables are not secured). | Fiber cable are not secured. | Cable Dressing | Fiber
Ericsson rectifier (battery backup is weak) &amp; Emerson rectifier (battery backup) is medium/observation. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
6 battery cells are weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Jumper cables required to arranged on the tower ladder. | Tower Ladder Cables Need Arrangement | Cable Dressing | Tower
Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site have no battery backup /shelter | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Fence is damaged / OT is a host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Emerson rectifier at site |  | DESIGN ISSUE | DESIGN ISSUE
BTS Room Seepage and cracking observed |  | CIVIL_WORK | Shelter
some nodes connected to AC directly |  | DESIGN ISSUE | DESIGN ISSUE
Two battery strings in different two rectifiers are zero |  | BATTERY BACKUP | BATTERY BACKUP
There is o fixed ladder to reach RT antenna |  | DESIGN ISSUE | DESIGN ISSUE
fiber cables arrangement is required | Fiber cable are not secured. | Cable Dressing | Fiber
some battery cells are fail and need to replace in booth two rectifiers |  | BATTERY BACKUP | BATTERY BACKUP
One of the main grounding cables is cut inside the shelter |  | Grounding | Grounding
There is no safe ladder to teach antenna |  | DESIGN ISSUE | DESIGN ISSUE
Site battery banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
OD power cable duct is rusted |  | OTHERS | Other
site portable ladder is not safe to use for single worker visit |  | CIVIL_WORK | RT Ladder
Site Battery installation date tag is missing |  | Labeling | Labeling
some RRU connectors waterproofing is missing |  | OTHERS | Other
there is no safe ladder to reach RT antenna |  | DESIGN ISSUE | DESIGN ISSUE
APM OD cabinet Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
some grounding cables are cut |  | Grounding | Grounding
one rectifier battery banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site battery backup is zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
tower legs grounding not installed |  | Grounding | Grounding
MANUAL MODE/RENTAL DG AT SITE |  | DESIGN ISSUE | DESIGN ISSUE
Site housekeeping is required /OT is a host | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
some OD grounding cables disconnected |  | Grounding | Grounding
RT ladder need to be fixed properly from upper end |  | CIVIL_WORK | RT Ladder
BTS room wall seepage is there |  | CIVIL_WORK | Shelter
Fueling theft issue |  | OTHERS | Other
mobilized DG and fuel tank are there |  | Extra Material | Extra Material
Some grounding cables are disconnected and MW pole grounding cable is damage |  | Grounding | Grounding
RT ladder need to be fixed properly from upper anchor points |  | CIVIL_WORK | RT Ladder
some battery cells are fail and need to replace | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Rectifier 1 is having 6 faulty battery cells | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Cracking is observed on BTS roll walls |  | CIVIL_WORK | Shelter
Meter box door lock is broken |  | OTHERS | Other
other vendor rectifier is at site |  | DESIGN ISSUE | DESIGN ISSUE
Site battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Some alarms connected manually |  | OTHERS | Other
Site battery banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Shelter body is having partial rust |  | CIVIL_WORK | Shelter
Site battery backup banks re weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
roxtech not sealed properly |  | OTHERS | Other
AC1 is not working | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
one battery cell is fault |  | BATTERY BACKUP | BATTERY BACKUP
Many cartons stored inside the room |  | Extra Material | Extra Material
ID fiber cables not arranged properly | Fiber cables not arranged properly | Cable Dressing | Fiber
meter box glass is broken and panel is dirty need to clean |  | OTHERS | Main DB
Fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Infilink is connecting to the AC directly. |  | DESIGN ISSUE | DESIGN ISSUE
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Boundary wall cracking |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
1. Fiber lying on ground (PT did activity for fiber connectivity at site ) | Fiber cables not arranged properly | Cable Dressing | Fiber
Lightning rod cable is missing /OT is a host |  | Grounding | Grounding
Tower painting is required /OT is a host |  | CIVIL_WORK | Tower
lightning rod is missing /OT is a host |  | Grounding | Grounding
Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
MW Dish at site /Belong s to Omantel |  | Extra Material | Extra Material
tower is completely rusted and foundation having major civil issues |  | CIVIL_WORK | Tower
cracking - corrosion and damage |  | CIVIL_WORK | Tower
Cable tray is totally rusted |  | CIVIL_WORK | Cable Tray
Tower Ladder physical condition is not safe to climb |  | CIVIL_WORK | Tower
shelter body is rusted |  | CIVIL_WORK | Shelter
A/C OD Units are rusted | Both A/C ODU is Rusty | AIR_CONDITIONER | AIR CONTIONER ODU
Fiber cable not proper arrange ATN to OSN | Fiber cables not arranged properly | Cable Dressing | Fiber
Boundary wall supports rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower Support steel wire rusty |  | CIVIL_WORK | Tower
Shelter Base rusty |  | CIVIL_WORK | Shelter
Extra material inside the room. |  | Extra Material | Extra Material
1 operational node is connected to the AC directly. |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cables are nor secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Rectifier battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
ID &amp; OD fiber cables are not secured. | Fiber cable are not secured. | Cable Dressing | Fiber
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
pathway repairing is required |  | CIVIL_WORK | PATHWAY DAMAGE
RT Spiral ladder stairs totally rusted |  | CIVIL_WORK | RT Ladder
only one battery bank available at site |  | BATTERY BACKUP | BATTERY BACKUP
fence is damaged /OT is a host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Both DG and fuel tank are not grounded |  | DG ISSUES | DG ISSUES
Pathway repairing is required |  | CIVIL_WORK | PATHWAY DAMAGE
Battery missing alarm |  | EXTERNAL ALARM | EXTERNAL ALARM
Site battery backup banks theft / Zero battery | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Boundary wall is cracked and need civil action |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra Material left at site (Pole). |  | Extra Material | Extra Material
boundary wall having minor Cracks |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Delta cabinet AC is faulty |  | DELTA CABINET | AIR_CONDITIONER
Extra Material (V-sat dish- Pole- &amp; V-sat receiver). |  | Extra Material | Extra Material
shelter body cracking is there |  | CIVIL_WORK | Shelter
Air conditions are at shelter roof and no access ladder to it. |  | DESIGN ISSUE | DESIGN ISSUE
Shelter is rusted |  | CIVIL_WORK | Shelter
NO FENCE HILLTOP |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
DAMAGED WASHED AWAY IN RAIN |  | CIVIL_WORK | Other
Emerson rectifier is at site |  | DESIGN ISSUE | DESIGN ISSUE
Site battery backup is zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
DG canopy and Fueling tank is rusted |  | DG ISSUES | DG ISSUES
Main gate rusted /OT Site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
main grounding cable of the tower is cut |  | Grounding | Grounding
OD pipes need to be isolated properly | OD pipes insulation is required | AIR_CONDITIONER | AIR CONTIONER ODU
One Battery backup bank is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DG and external tank are not grounded and both are located outside site boundary wall |  | Design Issue | Design Issue
Minor cut in wire mesh fence close to DG fuel tank . |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Prim DG power supply cable is not properly routed |  | Design Issue | Design Issue
Site Battery backup banks are weak and need to replace | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DG and external tank are not grounded |  | Design Issue | Design Issue
bus bar greasing is required |  | OTHERS | Other
DG and external fuel tank are not grounded |  | Design Issue | Design Issue
DG and external fuel tank are not grounded |  | Design Issue | Design Issue
site boundary wall cracking is observed |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
DG and external fuel tank are not grounded |  | Design Issue | Design Issue
DG and external fuel tank are not grounded |  | Design Issue | Design Issue
OD Bus bars require greasing |  | OTHERS | Other
Tower ladder base foundation cracking /OT Tower |  | CIVIL_WORK | Tower
one battery backup bank is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
one battery bank is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra materials stored at site ( VSAT DISHES AND RACKS ) |  | Extra Material | Extra Material
DG and its external tank are not grounded |  | Design Issue | Design Issue
DG and its external tank are not grounded |  | Design Issue | Design Issue
DG and external fuel tank are not grounded |  | Design Issue | Design Issue
External fuel tank is rusty |  | DG ISSUES | DG ISSUES
Site boundary wall painting need to maintain |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site boundary wall cracking and painting need to maintain. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
DG and external fuel tank are not grounded |  | Design Issue | Design Issue
Site access pathway is damaged |  | CIVIL_WORK | PATHWAY DAMAGE
Tower lightning rod cable is cut--Passive repeater |  | Grounding | Grounding
Tower Legs grounding is missing -Passive repeater |  | Grounding | Grounding
Site access pathway is damaged |  | CIVIL_WORK | PATHWAY DAMAGE
Site battery bank is faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
VSAT cables are not properly routed inside pipe |  | OTHERS | Other
Site is located on top of high mountain with no identified pathway since integration and need 3 hrs to access with nearby farm owner support for road guidance |  | CIVIL_WORK | PATHWAY DAMAGE
Site Battery banks are fail and need to replace | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
gate razor is damaged/OT Site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site Access Pathway is damaged |  | CIVIL_WORK | PATHWAY DAMAGE
Lightning rod cable is missing |  | Grounding | Grounding
Site Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Main gate razor wire is damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shelter body is rusted |  | CIVIL_WORK | Shelter
Meter box glass is broken |  | OTHERS | Main DB
cable ladder has corrosion |  | CIVIL_WORK | Cable Tray
Gate is rusted and need to repair |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower painting is required |  | CIVIL_WORK | Tower
Meter box glass is broken |  | OTHERS | Main DB
Prim DG power sully cable is not properly routed and protected |  | Design Issue | Design Issue
DG and external fuel tank are not grounded |  | Design Issue | Design Issue
Site Fence is collapsed |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
DG and external fuel tank are not grounded |  | Design Issue | Design Issue
DG and external fuel tank are not grounded |  | Design Issue | Design Issue
fuel tank is rusted |  | DG ISSUES | DG ISSUES
Prim DG power supply cable is not routed and protected properly |  | Design Issue | Design Issue
COW Site Boundary fence is collapsed |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
DG and external tank are not rounded |  | Design Issue | Design Issue
Prim DG power supply cable is not protected and routed properly |  | Design Issue | Design Issue
DG and external tank are not grounded |  | Design Issue | Design Issue
Operational nodes connected with AC directly |  | Design Issue | Design Issue
TN power redundancy cable is missing |  | Design Issue | Design Issue
Site battery banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DG and external tank are not grounded |  | Design Issue | Design Issue
External fuel tank is rusted |  | DG ISSUES | DG ISSUES
MW antenna at site premises /Project team |  | Extra Material | Extra Material
DG and external tank are not grounded |  | Design Issue | Design Issue
DG and external tanks are not grounded |  | Design Issue | Design Issue
DG and external tank are not grounded |  | Design Issue | Design Issue
DG and external tank are not grounded |  | Design Issue | Design Issue
DG and external tank are not grounded |  | Design Issue | Design Issue
Fencing is rusted &amp; damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
One battery is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fire Alarm system &amp; smoke detector is not installed . |  | Design Issue | Design Issue
Couples of batteries are weak. | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
House keeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Boundary Wall having cracks. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower lightning rod cable is cut. |  | Grounding | Grounding
Main gate paint is required. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Boundary wall have some minor cracks. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site boundary wall is cracked |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
minor house keeping required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Outdoor cabinet concrete base is not in level |  | CIVIL_WORK | Foundation
Tower need painting |  | CIVIL_WORK | Tower
Tower is rusted - MOD Island site and capturing OD Photos is not allowed |  | CIVIL_WORK | Tower
Shelter body is rusted - Site is Island MOD and capturing OD photos is not allowed |  | CIVIL_WORK | Shelter
Prim DG power supply cable is not routed and protected properly |  | Design Issue | Design Issue
DG and external tanks are not grounded |  | Design Issue | Design Issue
Site Main Earth Pit are missing ( Only Rod one available ) |  | Grounding | Grounding
Main power supply cable is not protected properly |  | Design Issue | Design Issue
Site logbook is missing |  | LOG BOOK | LOG BOOK
Feeder cables are not Grounded |  | Grounding | Grounding
DG and external tank are not grounded |  | Design Issue | Design Issue
Site Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Paint is required. |  | CIVIL_WORK | Tower
Meter box base is damage . |  | CIVIL_WORK | Foundation
Site boundary wall cracking is observed |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower legs grounding is missing /OT is a host |  | Grounding | Grounding
Site Battery Backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site BB is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Tower painting is required |  | CIVIL_WORK | Tower
Small bushes at site so housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Tower Wire concrete Blocks imbalanced because of Site surroundings ground level compression/Civil action is required |  | CIVIL_WORK | Compound Damage
Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DG and external tank are not grounded |  | Design Issue | Design Issue
Site fencing fall down |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fiber cable is not secure. | Fiber cable are not secured. | Cable Dressing | Fiber
1)Dismantle batteries &amp; Ericsson rectifier Extra material Available at site. |  | Extra Material | Extra Material
Power DB grounding cable is not connected with bus bar |  | GROUNDING | GROUNDING
Prime DG generating so much smoke. |  | DG Issues | DG Issues
Tower lightning rod cable is cut\r\nTower bus bar cable is missing |  | GROUNDING | GROUNDING
Boundary wall have minor cracks. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower bus bar grounding is missing. |  | GROUNDING | GROUNDING
Tower lightning rod cable is cut |  | GROUNDING | GROUNDING
DG Body is rusted. |  | DG ISSUES | DG Issues
DG is not working. |  | DG ISSUES | DG Issues
Rooftop pole grounding is missing. |  | GROUNDING | GROUNDING
fencing is minor damage. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Rooftop room door is damage. |  | CIVIL_WORK | Shelter
Razor wire are damage. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower lightning rod cable is not connected with Earth pit |  | GROUNDING | GROUNDING
Tower leg grounding is not connected with Earth pit |  | GROUNDING | GROUNDING
DG tank is rusted |  | DG ISSUES | DG Issues
Site Battery Backup is weak / Site is located inside quram royal office and as per Security rules it is prohibited to access the Royal area with mobile phone or laptop . | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra Materials available at site /Site is located inside quram royal office and as per Security rules it is prohibited to access the area with mobile phone or laptop . |  | Extra Material | Extra Material
Fiber cables need to arrange and protect properly | Fiber cable are not secured. | Cable Dressing | Fiber
Batteries not detected alarm is showing on IBS rectifier controller of Sector A |  | DESIGN ISSUE | DESIGN ISSUE
ID Site IBS rectifier battery back up is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Lightning rod cable is missing |  | GROUNDING | GROUNDING
Tower grounding cables stolen |  | GROUNDING | GROUNDING
panel Door grounding cable is disconnected |  | GROUNDING | GROUNDING
Boundary Wall is having minor cracks. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Emerson Rectifier is in operational at site |  | DESIGN ISSUE | DESIGN ISSUE
Site logbook is missing - Site is located in Royal palace IZZ . |  | Log Book | Log Book
Site boundary wall is cracked and need painting |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra material are available at site(Mount- Antenna- RRu) |  | Extra Material | Extra Material
Outdoor cables required to arrange on cable tray. |  | Cable Dressing | CABLE DRESSING
Ericsson pbc6500 \\r\\nrectifier are available at site and its active . |  | DESIGN ISSUE | DESIGN ISSUE
Tower cabel arrangement is required | Tower Cables arrangement is required | Cable Dressing | Tower
Emerson rectifier is working at sit |  | DESIGN ISSUE | DESIGN ISSUE
Site boundary wall is having minor cracking |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fiber cables is not properly arrange. | Fiber cables not arranged properly | Cable Dressing | Fiber
Boundary wall have minor cracks. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
BTS door lock is not working. |  | DELTA CABINET | DOOR LOCK
BTS cooling system is not working. |  | DELTA CABINET | AIR_CONDITIONER
Tower lighting earth rod cable is missing. |  | GROUNDING | GROUNDING
fiber cables are not properly routed. | Fiber cables not arranged properly | Cable Dressing | Fiber
Room have sea-page issue |  | CIVIL_WORK | Shelter
SITE BATTERY BACKUP BANKS IS ZERO | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Tower bus-bar grounding cable is missing |  | GROUNDING | GROUNDING
Couples of battery is weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Main power meter box door is broken | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
Site is zero Battery Backup | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Site Is Zero Battery Backup -IBS Airport Site |  | BATTERY BACKUP | BATTERY BACKUP
Pathway damage |  | CIVIL_WORK | PATHWAY DAMAGE
AC1 is not working. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Aviation light system board is not working. | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
Site have no pathway |  | CIVIL_WORK | PATHWAY DAMAGE
Boundary wall have cracks |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Gate Razor wire is damage . |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Logbook is missing |  | Log Book | Log Book
V-sat dish basement is not concreted |  | DESIGN ISSUE | DESIGN ISSUE
Equipment is connected on AC power (business customer) |  | DESIGN ISSUE | DESIGN ISSUE
Greasing is required |  | OTHERS | OTHER
Batteries bank is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Equipment is connected on AC power |  | DESIGN ISSUE | DESIGN ISSUE
House keeping is required. | Site Housekeeping is required | HOUSEKEEPING | HouseKeeping
Microwave grounding is missing |  | Grounding | Grounding
No safe ladder is available to ac door units |  | DESIGN ISSUE | DESIGN ISSUE
Equipment is connected on AC power |  | DESIGN ISSUE | DESIGN ISSUE
Boundary wall have minor cracks. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
BTS door is damage |  | DELTA CABINET | DOOR LOCK
NO safe ladder is available to reached at RRU &amp; Antenna |  | DESIGN ISSUE | DESIGN ISSUE
BTS door lock is not working . |  | DELTA CABINET | DOOR LOCK
Ericsson rectifier are available at site |  | DESIGN ISSUE | DESIGN ISSUE
Couples of Batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
BTS door lock is faulty |  | DELTA CABINET | DOOR LOCK
IF cable &amp; jumpers cables are not routed properly. | IF cables not arranged properly | CABLE DRESSING | IF
BTS door cooling system is faulty. |  | DELTA CABINET | AIR_CONDITIONER
Cleaning is required. |  | OTHERS | Other
Fiber cables are not properly routed. | Fiber cables not arranged properly | Cable Dressing | Fiber
Outdoor cables are not properly arrange |  | Cable Dressing | CABLE DRESSING
Pathway damage |  | CIVIL_WORK | PATHWAY DAMAGE
Tower lightning rod cable is cut. |  | Grounding | Grounding
Tower leg grounding cable is missing. |  | Grounding | Grounding
Ladder is not available to reached antenna and RRU. |  | DESIGN ISSUE | DESIGN ISSUE
Battery back up of site is Weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fiber cables arrangement is required | Fiber cables not arranged properly | Cable Dressing | Fiber
Equipment is connected on AC power. |  | DESIGN ISSUE | DESIGN ISSUE
Equipment is connected on AC power. |  | DESIGN ISSUE | DESIGN ISSUE
Equipment is connected on AC power . |  | DESIGN ISSUE | DESIGN ISSUE
Equipment is connected on AC power |  | DESIGN ISSUE | DESIGN ISSUE
Equipment is connected on AC power. |  | DESIGN ISSUE | DESIGN ISSUE
Equipment is connected on AC power. |  | DESIGN ISSUE | DESIGN ISSUE
Equipment is connected on AC power. |  | DESIGN ISSUE | DESIGN ISSUE
Fiber cables is not properly routed | Fiber cables not arranged properly | Cable Dressing | Fiber
Batteries are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fiber cables is not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Batteries have zero backup |  | BATTERY BACKUP | BATTERY BACKUP
No safe ladder is available to ac door units |  | DESIGN ISSUE | DESIGN ISSUE
Pathway damage |  | CIVIL_WORK | PATHWAY DAMAGE
Aviation board is faulty . | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
Tower lighting rod cable is cut |  | Grounding | Grounding
Aviation board is faulty | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
Gate pillar is moving and need cement to fix it |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower lighting rod cable is cut |  | Grounding | Grounding
Extra material are available at site (microwave dish) |  | Extra Material | Extra Material
Main gate is rusted and damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower lighting rod cable is cut |  | Grounding | Grounding
Tower leg grounding is not connected with earth pit |  | Grounding | Grounding
Shelter door lock is not working |  | OTHERS | Shelter
Couples of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Fencing is damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
No car access pathway since site integration |  | CIVIL_WORK | PATHWAY DAMAGE
Boundary wall have minor cracks |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower ladder foundation is crack |  | CIVIL_WORK | Foundation
Extremely pathway damage |  | CIVIL_WORK | PATHWAY DAMAGE
Equipment is connected on AC power |  | DESIGN ISSUE | DESIGN ISSUE
Boundary wall is not Available |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Boundary wall is not available |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Boundary wall have minor cracks. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Greasing is required |  | OTHERS | Other
Cable tray is not installed |  | DESIGN ISSUE | DESIGN ISSUE
There is no installed Site fence |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Boundary wall cracking need to maintain |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site islocated inside industial zone ans surrounded by heavy equipment |  | DESIGN ISSUE | DESIGN ISSUE
Boundary wall is cracked |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Boundary Wall near to DG got black due to smoke of Genset |  | DESIGN ISSUE | DESIGN ISSUE
Shotto Batteries and one Rectifier |  | Extra Material | Extra Material
Lightning rod cable is missing |  | Grounding | Grounding
one tower Bracket need to fix proprly |  | CIVIL_WORK | Tower
GI Pole bolts and nuts are rusted |  | CIVIL_WORK | Tower
GI pole climbing rods are not available |  | CIVIL_WORK | Tower
Power OFF Repeater |  | DESIGN ISSUE | DESIGN ISSUE
Power OFF Repeater |  | DESIGN ISSUE | DESIGN ISSUE
Equipment connected directly to AC |  | DESIGN ISSUE | DESIGN ISSUE
Antennas are located outside building so all are not accessible manually by maintenance team so crane is required for any troubleshooting |  | DESIGN ISSUE | DESIGN ISSUE
OD MW link grounding cable is missing |  | Grounding | Grounding
Power Meter Door Locks Broken |  | CIVIL_WORK | Main DB
Temperature sensor is not installed /OD Cabinet |  | DELTA CABINET | Sensor
OD Delta cabinet lock is damaged |  | DELTA CABINET | DOOR LOCK
RT Poles Grounding Cables are missing |  | Grounding | Grounding
Spiral ladder is rusted |  | CIVIL_WORK | RT Ladder
Site battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Equipment is connected on AC power |  | DESIGN ISSUE | DESIGN ISSUE
Equipment is connected on AC power. |  | DESIGN ISSUE | DESIGN ISSUE
Equipment is connected on Ac power |  | DESIGN ISSUE | DESIGN ISSUE
Extra materials ( Mounts and antennas ) placed beside shelter |  | Extra Material | Extra Material
Shelter body is having minor rust |  | CIVIL_WORK | Shelter
Shelter Roxtech sealing is required |  | OTHERS | Other
One battery string is weak and rest are medium | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
some OD grounding cables are cut |  | Grounding | Grounding
Site Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra dismantled cable need to remove from the site |  | Extra Material | Extra Material
TX Delta cabinet door lock is faulty |  | DELTA CABINET | DOOR LOCK
Roxtech sealing is required |  | OTHERS | Other
One battery backup bank is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Beehive placed just beside OD LTE cabinet / HSE Risk need pest control team to clear this hazard |  | OTHERS | Other
BTS Room door Numerical lock is faulty |  | OTHERS | Other
OD AC units metallic base frame is rusted |  | OTHERS | Other
power meter box door lock s damaged and glass is broken |  | CIVIL_WORK | Main DB
shelter body is rusted |  | CIVIL_WORK | Shelter
Site battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
OD delta cabinet lock is faulty |  | DELTA CABINET | DOOR LOCK
No safe ladder is available to ac door units. |  | DESIGN ISSUE | DESIGN ISSUE
Equipment is connected on AC power |  | DESIGN ISSUE | DESIGN ISSUE
Equipment is connected on Ac power. |  | DESIGN ISSUE | DESIGN ISSUE
Equipment is connected on Ac power. |  | DESIGN ISSUE | DESIGN ISSUE
There is no boundary Fence installed at site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
sand dunes at site premises |  | CIVIL_WORK | Sand
shelter entrance Step basement is missing |  | CIVIL_WORK | Shelter
Shelter door lock is faulty |  | CIVIL_WORK | Shelter
Logbook is missing |  | Log Book | Log Book
Site floor is not leveled properly &amp;V-sat Dish basement is fixed by blocks |  | CIVIL_WORK | Compound
Equipment is connected directly to AC |  | DESIGN ISSUE | DESIGN ISSUE
Equipment is connected to AC directly |  | DESIGN ISSUE | DESIGN ISSUE
There is no Fence &amp; Gate installed for site access security |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
There is no fence at site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
GI pole nuts and bolts are rusted/also pole climbing rod is damage due to corrosion |  | CIVIL_WORK | Tower
3G system is connected directly to AC |  | DESIGN ISSUE | DESIGN ISSUE
Battery backup banks are zero for OD sectors |  | BATTERY BACKUP | BATTERY BACKUP
There was no earth bus bar and Earth cable was rolled instead |  | DESIGN ISSUE | DESIGN ISSUE
MOD tower need to paint |  | CIVIL_WORK | Tower
MOD Tower is rusted |  | CIVIL_WORK | Tower
Extremely pathway damage |  | CIVIL_WORK | PATHWAY DAMAGE
Tower lightning rod cable is cut--Passive repeater |  | Grounding | Grounding
Tower leg grounding is missing |  | Grounding | Grounding
Equipment is connected on Ac power |  | DESIGN ISSUE | DESIGN ISSUE
Spiral Rooftop ladder is rusted and civil action is required |  | CIVIL_WORK | RT Ladder
BTS Room door need to repair |  | CIVIL_WORK | Indoor Shelter
Main Gate is ahving Major rusty and need to replace |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
RT Ladder is rusted |  | CIVIL_WORK | RT Ladder
Site Battery Backup Banks are zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Batteries backup is zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Tower lighting rod cable is cut. |  | Grounding | Grounding
Site Boundary wall seepage is existing |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Delta OD Cabinet cooling system is faulty |  | DELTA CABINET | AIR_CONDITIONER
Gate is having a little rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Aviation light alarm is on board /Noisy alarm | Aviation light system is not working, Need Replace | AVIATION_LIGHT | AVIATION LIGHT BOARD
Lightning rod cable is disconnected from down side |  | Grounding | Grounding
Main gate is having rust and boundary wall is cracked |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Dismantled Hybrid DG system with external fuel tank existing at the site |  | Extra Material | Extra Material
Site floor leveling is not balance - wall is cracked and foundation is not ok |  | CIVIL_WORK | Compound
DG canopy is rusted |  | DG Issues | DG Issues
SDG failed to start due to Low fueling Issue |  | DG Issues | DG Issues
Lightning rod cable is cut |  | Grounding | Grounding
Compressor fault - Battery not detected alarms are showing on rectifier controller |  | External Alarm | External Alarm
Battery backup is zero /Not detected | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Site fence is having cut so site is easy to access through it /OT is Host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra materials at site /Roll of cable |  | Extra Material | Extra Material
Lightning rod cable is missing |  | Grounding | Grounding
Batteries poles need to clean |  | OTHERS | Other
Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shelter Paint is required |  | CIVIL_WORK | Indoor Shelter
Main power meter box is completely rusted and damaged | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
Main gate is rusted and rods are damaged due to this corrosion |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fence Supporting rods are damaged/broken due to rust |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Gate is Damaged more than 50% |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower paint is required |  | CIVIL_WORK | Tower
One BB string is faulty | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
OD Delta Cabinet Air con system is faulty |  | DELTA CABINET | AIR_CONDITIONER
Delta Cabinet Filter is faulty and need to replace |  | DELTA CABINET | Delta_Filter
OD Delta cabinet hand held lock is damaged |  | DELTA CABINET | DOOR LOCK
OD Delta Cabinet one rectifier module faulty |  | DELTA CABINET | Rectifier Module
OD Delta Cabinet Door air filter faulty |  | DELTA CABINET | Delta_Filter
OD Delta Cabinet lock faulty |  | DELTA CABINET | DOOR LOCK
Equipment connected to AC power |  | Design Issue | Design Issue
OG rectifier battery backup weak due to bank 1 cell faulty | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra material available at site old Ericsson material and old batteries |  | Extra Material | Extra Material
Lightning rod cable is missing |  | Grounding | Grounding
Tower Legs grounding is stolen |  | Grounding | Grounding
Site soil leveling close to tower leg need to maintain |  | CIVIL_WORK | Compound
Small cracking in boundary wall |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site Battery backup banks are fail | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
No safe ladder is available to reach at Antenna &amp; RRU |  | Design Issue | Design Issue
Tower lightning rod cable is cut. |  | Grounding | Grounding
Boundary wall are damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Batteries found faulty &amp; disconnected . | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Tower lightning rod is broken . |  | Grounding | Grounding
Equipment is connected on Ac power |  | Design Issue | Design Issue
Couples of batteries are weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HouseKeeping
Tower main earth cable is cut and main earth pits foundation need to maintain |  | Grounding | Grounding
Lightning rod cable is disconnected from the top and need to fix properly along the tower |  | Grounding | Grounding
power meter box foundation is broken and need civil repairing |  | CIVIL_WORK | Foundation
Delta Cabinet door internal Air con is faulty |  | DELTA CABINET | AIR_CONDITIONER
Equipment is connected on Ac power |  | Design Issue | Design Issue
Battery bank have zero backup | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
BTS cooling system is not working |  | DELTA CABINET | AIR_CONDITIONER
1-Delta cabinet filter need to change .\r\n2-Cabinet cleaning is required. |  | DELTA CABINET | Delta_Filter
BTS door lock is faulty. |  | DELTA CABINET | DOOR LOCK
No safe ladder is available to reach antenna &amp; rru |  | Design Issue | Design Issue
Battery bank have zero backup | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Delta cabinet air-con system is faulty |  | DELTA CABINET | AIR_CONDITIONER
BTS door cooling system is faulty |  | DELTA CABINET | AIR_CONDITIONER
BTS door lock is not working |  | DELTA CABINET | DOOR LOCK
All batteries have zero backup | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Rectifier controller is having alarm. |  | DELTA CABINET | Rectifier Module
battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site Battery Backup Banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Tower Leg cracking /OT Tower |  | CIVIL_WORK | Tower
Main gate is rusted and require full paint |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Distribution penal is rusted and need to replace |  | CIVIL_WORK | Main DB
Boundary wall cracking and need civil repairing |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
pathway to hill top tower need to be repaired |  | CIVIL_WORK | PATHWAY DAMAGE
There is no safe ladder to reach to RT antenna |  | Design Issue | Design Issue
Extra MW dish available at site |  | Extra Material | Extra Material
TDD cabinet Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Huawei Switch device is on AC power |  | Design Issue | Design Issue
Genset is not working as its under rated /Low Capacity |  | DG Issues | DG Issues
Shelter still available - while it is shifted to OD hybrid &amp; Also Vsat foundation still available while it is shifted to MW |  | Extra Material | Extra Material
Tower Painting is required |  | CIVIL_WORK | Tower
Minor cracks on one tower leg foundation and ladder foundation |  | CIVIL_WORK | Tower
Batteries are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site Battery Backup Banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Gate latches are broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Aviation light board is faulty | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION LIGHT BOARD
Site Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site Battery Backup banks are faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Rooftop grounding cable is cut. |  | Grounding | Grounding
No proper ladder to reached Antenna &amp; RRU |  | Design Issue | Design Issue
Tower lightning rod cable is cut |  | Grounding | Grounding
Antenna &amp; RRU grounding cable is stolen |  | Grounding | Grounding
All batteries have zero backup | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Site id label is not as per standard |  | Design Issue | Design Issue
Extra material are available at site(Mount) |  | Extra Material | Extra Material
Tower lightning rod cable is cut. |  | Grounding | Grounding
BTS cooling system is not working |  | DELTA CABINET | AIR_CONDITIONER
Delta door lock is faulty. |  | DELTA CABINET | DOOR LOCK
Equipment is connected on AC power. |  | Design Issue | Design Issue
Fencing damage due to heavy stone fall down |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower lightning rod cable is cut |  | Grounding | Grounding
Emerson Rectifier is operational at the site |  | Design Issue | Design Issue
Site Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HouseKeeping
Main gate padlock is missing /OT Site | Site main gate padlock is missing | PADLOCK | Padlock
Site Batteries are stolen | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Tower lightning rod cable is cut |  | Grounding | Grounding
Outdoor cables are not properly arrange on cable tray |  | Cable Dressing | CABLE DRESSING
Extra PBC6500 Cabinet inside shelter |  | Extra Material | Extra Material
All batteries are stolen. | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
BC equipment is connect on AC power |  | Design Issue | Design Issue
All batteries have zero backup | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
All batteries are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Tower lightning rod cable is cut |  | Grounding | Grounding
Shelter is rusted &amp; need major civil action |  | CIVIL_WORK | Shelter
All batteries have zero backup | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
All batteries are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
All batteries have zero backup | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
All batteries have zero backup | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
BTS cooling system is faulty |  | DELTA CABINET | AIR_CONDITIONER
Rectifier 1 Battery backup banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site is located at bousher data center. There are some extra materails placed inside site terriority and seems some solar street lights material- poles etc |  | Extra Material | Extra Material
Both shelter A/C are in good condition and on manual mode since long due to equipment requirement |  | Design Issue | Design Issue
All batteries have zero backup &amp; swelled | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Boundary wall have minor cracks |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Razor wire is loose need to repair . |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shelter floor cleaning i required . |  | OTHERS | Other
Tower lightning rod cable is cut |  | Grounding | Grounding
Wimax battery backup is zero | TDD/WiMax Battery Backup is Zero/Dead | BATTERY BACKUP | TDD/WiMax
Site Battery Backup Banks are Weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
There is no fixed ladder to reach RT Antenna |  | Design Issue | Design Issue
Site Battery Backup Banks are Zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Site Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | House Keeping
Site Battery Backup Banks are Zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Wimax cabinet batteries have zero backup | TDD/WiMax Battery Backup is Zero/Dead | BATTERY BACKUP | TDD/WiMax
Customer link not as per standard |  | Design Issue | Design Issue
Site main entrance gate is damage. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
All batteries have zero backup | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Delta cabinet Ac is faulty. |  | Delta Cabinet | Air Conditioner
Delta Outdoor cabinet door lock is damage |  | Delta Cabinet | Door Lock
Extra material are available at site ( Antenna &amp; mount) |  | Extra Material | Extra Material
Equipment is connected on AC power |  | Design Issue | Design Issue
All batteries are weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Equipment is connected on AC power |  | Design Issue | Design Issue
All batteries are weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Delta cabinet ac is not working |  | Delta Cabinet | Air Conditioner
Delta outdoor cabinet lock is faulty |  | Delta Cabinet | Door Lock
High temperature alarm is loop |  | Delta Cabinet | External Alarm
Rectifier controller is having alarm. |  | Delta Cabinet | Rectifier
All batteries have zero backup | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Delta outdoor cabinet Ac is faulty |  | Delta Cabinet | Air Conditioner
Delta cabinet filter need to change |  | Delta Cabinet | Air Conditioner
High temperature alarm is loop. |  | Delta Cabinet | External Alarm
No safe ladder to reached Antenna maintenance |  | Design Issue | Design Issue
Extra material are available (Dismantled rectifier ) |  | Extra Material | Extra Material
Equipment is connected on AC power |  | Design Issue | Design Issue
All batteries have zero backup | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
BTS cooling system is faulty. | BTS Cooling system is faulty | AIR_CONDITIONER | AIR_CONDITIONER
Equipment is connected on ac power. |  | Design Issue | Design Issue
Main gate &amp; fencing is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Rectifier display is not working . |  | Delta Cabinet | Rectifier
Delta cabinet ac is faulty |  | Delta Cabinet | Air Conditioner
Delta cabinet filter need to change |  | Delta Cabinet | Air Conditioner
Power Alarm is loop. |  | Delta Cabinet | External Alarm
High temperature alarm is loop. |  | Delta Cabinet | External Alarm
Air-con alarm is loop |  | Delta Cabinet | External Alarm
There is no fixed safe ladder to reach antenna |  | Design Issue | Design Issue
Site Battery Backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site main gate is damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site boundary fence is having damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site Battery Backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra MW dish available at site |  | Extra Material | Extra Material
Prim DG power cable is not protected properly |  | DG ISSUES | DG Issues
Site Soil treatment is required |  | CIVIL_WORK | Compound
Battery backup string is weak | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
one side of the fence is damaged/ OT is a host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site foundation is having minor cracking /Civil action is required |  | CIVIL_WORK | Compound
Lightning rod cable is missing |  | Grounding | Grounding
Emerson rectifier is in operational mode at site |  | Design Issue | Design Issue
Main gate is broken /OT is a host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Sand dunes at site |  | CIVIL_WORK | Compound
Power meter bx glass is broken | Power meter Box glass missing | CIVIL_WORK | ACDB
Bus bar Grounding cable is cut |  | Grounding | Grounding
Antenna &amp;RRU grounding cable is cut |  | Grounding | Grounding
Equipment is connected on AC power |  | Design Issue | Design Issue
Microwave &amp; RRU Grounding cable is missing. |  | Grounding | Grounding
Fiber cables are not routed properly on cable tray | Fiber cables not arranged properly | Cable Dressing | Fiber
All batteries are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Couples of batteries are weak. | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Delta cabinet ac is not faulty . |  | Delta Cabinet | Air Conditioner
All batteries are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
All batteries have zero backup | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Fiber cable is not properly routed | Fiber cables not arranged properly | Cable Dressing | Fiber
Bus bar grounding cable is cut |  | Grounding | Grounding
No proper ladder is available to reached Antenna &amp; RRU maintenance |  | Design Issue | Design Issue
Couple of batteries are weak. | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
No proper ladder is available to reached Antenna &amp; RRU maintenance |  | Design Issue | Design Issue
No proper ladder is available to reached Antenna &amp; RRU maintenance |  | Design Issue | Design Issue
Wimax battery backup weak | TDD/WiMax Battery Backup is Weak | BATTERY BACKUP | TDD/WiMax
Extra material are available at site ( Microwave dish ) |  | Extra Material | Extra Material
Shelter wall pasted poster need to remove |  | CIVIL_WORK | Shelter
Equipment is connected on AC power. |  | Design Issue | Design Issue
Seepage found in BTS room |  | CIVIL_WORK | Shelter
Site main gate is rusted and rods are broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Sand dune at site which is blocking main gate |  | CIVIL_WORK | Sand
Lightning rod cable is cut at mid of the tower |  | Grounding | Grounding
Tower base cracking is observed |  | CIVIL_WORK | Tower
meter box is rusted |  | CIVIL_WORK | ACDB
phases cables need to be isolated properly inside power meter box / high risky condition |  | OTHERS | Other
Site battery backup is weak for both ID shelter &amp; OD LTE Cabinet | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site boundary Fence wire meshes are broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site main gate is fully rusted and demolished |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
OD grounding cables &amp; tower main grounding cables are cut |  | Grounding | Grounding
Main earth bit hole is damaged and earth kit need greasing as well as OD cabinet sun shield is broken |  | Grounding | Grounding
Shelter body is partially rusted |  | CIVIL_WORK | Shelter
OD LTE cabinet Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site Pathway need to repair /GF RF Repeater is switched OFF |  | CIVIL_WORK | PATHWAY DAMAGE
Extra Materials ( Old shelter and V-Sat)) available at site |  | Extra Material | Extra Material
Major housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | House Keeping
OD MW link grounding cable is cut |  | Grounding | Grounding
jumper waterproofing - Fiber junction box is broken &amp; bird home is built over antenna jumpers |  | OTHERS | Other
Delta Cabinet rectifier module is faulty |  | Delta Cabinet | Rectifier
Site Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
PDB is rusted |  | OTHERS | Other
boundary fence Pillars are rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Delta OD Cabinet Cooling system is faulty |  | Delta Cabinet | Air Conditioner
Delta OD Cabinet filter need to replace |  | Delta Cabinet | Air Conditioner
Delta Cabinet Door lock is faulty |  | Delta Cabinet | Door Lock
Prim DG power supply cable is not secured properly / also power cable is connected directly to Main power meter box not to MDB inside Room |  | DG ISSUES | DG Issues
Battery backup bank is faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Aviation light is not installed on Tower |  | Design Issue | Design Issue
External Fuel tank is rusted |  | DG ISSUES | DG Issues
Pathway repairing is required |  | CIVIL_WORK | PATHWAY DAMAGE
Battery cover broken |  | OTHERS | Other
Emerson rectifier is running in shelter |  | Design Issue | Design Issue
Alarms are not configured |  | Design Issue | Design Issue
Tower lightning rod is broken Need to repair . |  | Grounding | Grounding
Tower lightning rod cable is cut |  | Grounding | Grounding
Site Main gate is broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower paint is required |  | CIVIL_WORK | Tower
Shelter body/roof is damaged |  | CIVIL_WORK | Shelter
Site SDG is under rating |  | Design Issue | Design Issue
DG Body is rusted |  | DG ISSUES | DG Issues
Tower lightning rod cable is cut. |  | Grounding | Grounding
Tower leg grounding cable is cut |  | Grounding | Grounding
Tower lightning rod cable is cut |  | Grounding | Grounding
Tower lightning rod cable is cut. |  | Grounding | Grounding
All Site Grounding cables are stolen |  | Grounding | Grounding
Rectifier controller is faulty |  | Delta Cabinet | Rectifier
OD Delta Cabinet is faulty |  | Delta Cabinet | Door Lock
Pathway damage |  | CIVIL_WORK | PATHWAY DAMAGE
tower lightning rod cable is missing |  | Grounding | Grounding
All batteries are weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Pathway damage |  | CIVIL_WORK | PATHWAY DAMAGE
Couples of batteries are weak. | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
Tower lightning rod is cable is cut. |  | Grounding | Grounding
Site Pathway is damaged |  | CIVIL_WORK | PATHWAY DAMAGE
Need install safe fixed ladder instead of portable risky one |  | Design Issue | Design Issue
Site Battery Backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
One battery is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Main Gate latch is damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
GSM Antenna and external fuel tank pipes placed at site |  | Extra Material | Extra Material
Lightning rod cable is stolen |  | Grounding | Grounding
Site Battery Backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
OD delta cabinet door lock is faulty |  | Delta Cabinet | Door Lock
Rectifier number 2 battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Many of grounding cables are cut |  | Grounding | Grounding
Rectifier battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Lightning rod cable is cut |  | Grounding | Grounding
Shelter is partially rusty |  | CIVIL_WORK | Shelter
Main gate is rusted and boundary fence is partially damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
One battery backup string is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Bus bar grounding cable is cut. |  | GROUNDING | GROUNDING
Tower lightning rod cable is cut |  | GROUNDING | GROUNDING
Tower leg grounding cable is cut |  | GROUNDING | GROUNDING
Outdoor light is not working |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
OD pipes insulation is required | OD pipes insulation is required | AIR_CONDITIONER | AIR CONTIONER ODU
All batteries are weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
All are batteries are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
All batteries are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Grounding system is having an issue as building not earthed |  | GROUNDING | GROUNDING
TN is not installed properly |  | DESIGN ISSUE | DESIGN ISSUE
Meter Box glass is broken |  | CIVIL_WORK | Maing DB
Extra shelter at site after shifting to OD cabinet with Hybrid system |  | EXTRA MATERIAL | EXTRA MATERIAL
Extra shelter available as Site is shifted to OD with Hybrid system |  | EXTRA MATERIAL | EXTRA MATERIAL
Small damage in site boundary fence |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site main gate is rusted and having one rod damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
some bushes &amp; scarps need to remove outside site premises | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
site fence pillars rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower lightning rod cable is cut |  | GROUNDING | GROUNDING
Business customer equipment is connected on AC power. |  | DESIGN ISSUE | DESIGN ISSUE
All batteries are weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Delta outdoor cabinet ac is faulty |  | DELTA CABINET | AIR_CONDITIONER
Site battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Delta Cabinet Air-con system is faulty |  | DELTA CABINET | AIR_CONDITIONER
Delta door lock is faulty . |  | DELTA CABINET | DOOR LOCK
V-sat cables is not properly routed . | VSAT cables not arranged properly | CABLE DRESSING | CABLE DRESSING
Shelter door lock is damage. |  | CIVIL_WORK | SHELTER
Rectifier controller module is faulty. |  | RECTIFIER | RECTIFIER ALARMS
Door lock is damage |  | OD CABINET | DOOR LOCK
Batteries installation dates is missing. |  | LABELING | LABELING
Delta door lock is faulty |  | DELTA CABINET | DOOR LOCK
Bus bar grounding cable is cut. |  | GROUNDING | GROUNDING
Tower lightning rod cable is cut |  | GROUNDING | GROUNDING
No safe pathway is available to reached Antenna &amp; RRU maintenance |  | CIVIL_WORK | PATHWAY DAMAGE
Rack#0A03 Module is faulty. |  | RECTIFIER | RECTIFIER MODULE
Rack#01A03 Rectifier controller is having alarm |  | RECTIFIER | RECTIFIER ALARMS
Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Boundary wall have minor cracks. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
main power meter box glass is broken |  | CIVIL_WORK | Main DB
tower lightning rod cable is missing |  | GROUNDING | GROUNDING
Cable ladder rusted and base totally damage |  | CIVIL_WORK | CABLE TRAY
Ladder hanging Rail damage |  | CIVIL_WORK | CABLE TRAY
Extra old TXN cabinet |  | EXTRA MATERIAL | EXTRA MATERIAL
Site Battery Backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Bus bar grounding cable is cut. |  | GROUNDING | GROUNDING
Tower lighting rod cable is cut |  | GROUNDING | GROUNDING
Main power supply phase cable is not protected properly and need to be fixed on priority. | Main Power Cables not arranged properly | CABLE DRESSING | Power Cable
Main gate pillar is having alarm |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower lightning rod cable is cut |  | GROUNDING | GROUNDING
IF cable is not properly routed on cable tray. | IF cables not arranged properly | CABLE DRESSING | IF
Tower lightning rod cable is cut. |  | GROUNDING | GROUNDING
Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Delta outdoor ac is faulty |  | DELTA CABINET | AIR_CONDITIONER
Delta outdoor filter need to change . |  | DELTA CABINET | AIR_CONDITIONER
Delta door lock is damage. |  | DELTA CABINET | DOOR LOCK
Shelter door lock is faulty . |  | CIVIL_WORK | SHELTER
Numerical lock is not installed |  | CIVIL_WORK | SHELTER
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Tower lightning rod is cut. |  | GROUNDING | GROUNDING
Tower lightning rod cable is cut |  | GROUNDING | GROUNDING
Tower lightning rod cable is cut |  | GROUNDING | GROUNDING
One module is disconnected |  | RECTIFIER | RECTIFIER MODULE
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
One rectifier module is faulty |  | RECTIFIER | RECTIFIER MODULE
Delta cabinet filter need to change |  | DELTA CABINET | Delta_Filter
Tower lightning rod cable is cut. |  | GROUNDING | GROUNDING
Tower leg grounding is not connected with earth pit |  | GROUNDING | GROUNDING
Shelter door lock is faulty. |  | CIVIL_WORK | SHELTER
Power meter box is demolished. |  | CIVIL_WORK | Main DB
All batteries are weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fence is damage and need maintenance with civil action |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
New Logotimer softwer isnt working therefore both aircons are working on manual mode. | A/C LOGOTIMER SW Issue | AIR_CONDITIONER | LOGO TIMER
Antenna Sectors are not reachable for maintenance as its installed outside the building |  | DESIGN ISSUE | DESIGN ISSUE
Site Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
OD Delta Cabinet hand lock is broken |  | DELTA CABINET | DOOR LOCK
Tower legs foundation need civil action |  | CIVIL_WORK | TOWER
there is no fixed ladder to reach RT antennas |  | DESIGN ISSUE | DESIGN ISSUE
A/C2 is not working | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
one battery cell is faulty | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
One A/C is not working | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
one battery cell is faulty | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Outdoor Delta cabinet A/C is Faulty |  | DELTA CABINET | AIR_CONDITIONER
Site Battery backup is Faulty. | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Tower foundation is cracked |  | CIVIL_WORK | TOWER
small bushes need to clean | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
shelter body need painting |  | CIVIL_WORK | Indoor Shelter
Site Battery backup bank is Zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Main gate need painting |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Aviation light board is faulty | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION LIGHT BOARD
One AC not Working | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Ligntening Rod need proper adjusting |  | GROUNDING | GROUNDING
Small bushes need to be removed | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Greasing Required |  | OTHERS | OTHERS
Site ID is erased Need new sticker |  | LABELING | LABELING
Need labeling |  | LABELING | LABELING
need Labeling |  | LABELING | LABELING
Fuel Tank require Cleaning |  | DG ISSUES | DG ISSUES
Bank Performance weak need to be replaced | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Need labeling |  | LABELING | LABELING
CB labeling Required |  | LABELING | LABELING
Site Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Site battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site Foundation major civil repair is required |  | CIVIL_WORK | Compound
RT Spiral ladder is rusted and its door is broken |  | CIVIL_WORK | RT Ladder
Labeling is missing |  | LABELING | LABELING
All Battery backup banks are faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
all antenna poles not grounded |  | GROUNDING | GROUNDING
Extra dismantle RRUs found back side shelter in compound. |  | EXTRA MATERIAL | EXTRA MATERIAL
Extra project material inside shelter |  | EXTRA MATERIAL | EXTRA MATERIAL
Labeling is missing |  | LABELING | LABELING
Tower access to MW dish is not safe -Design Issue |  | DESIGN ISSUE | DESIGN ISSUE
Logbook is not available |  | Log Book | Log Book
saftey wire of tower nok |  | CIVIL_WORK | Tower
Fence Damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
LADDER BASE BROKEN |  | CIVIL_WORK | Cable Tray
Horizental ladder not install near rectifier cabinet for RRU power cables |  | CIVIL_WORK | Cable Tray
Tower Equipment not grounded |  | GROUNDING | GROUNDING
Tower Equipment not grounded |  | GROUNDING | GROUNDING
Rusted tower unsafe to climb |  | CIVIL_WORK | Tower
ROOF TOP SITE Ladder is undafe for climbing |  | DESIGN ISSUE | CIVIL_WORK
ROOF TOP SITE Ladder is undafe for climbing |  | DESIGN ISSUE | CIVIL_WORK
ROOF TOP SITE Ladder is undafe for climbing |  | DESIGN ISSUE | CIVIL_WORK
ROOF TOP SITE Ladder is undafe for climbing |  | DESIGN ISSUE | CIVIL_WORK
ROOF TOP SITE Ladder is undafe for climbing |  | DESIGN ISSUE | CIVIL_WORK
Rusted tower unsafe to climb |  | CIVIL_WORK | Tower
Rusted tower unsafe to climb |  | CIVIL_WORK | Tower
Palm tree leaves are not in good condition |  | CIVIL_WORK | Tower
Tower nut bolts are missing (Ladder Shaking) |  | CIVIL_WORK | Tower
MAIN GATE IS BROKEN |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Complete Outdoor and Indoor Paint Required |  | CIVIL_WORK | Paint Job
1 BATTERY BANK MISSING | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
TOWER GROUNDING STOLEN |  | GROUNDING | GROUNDING
Omantel tower ladder & supports are rusty |  | CIVIL_WORK | Ladder Broken
Tower Rusted |  | CIVIL_WORK | Tower
TOWER GROUNDING STATUS (STOLEN) |  | GROUNDING | GROUNDING
Tower base foundation damaged |  | CIVIL_WORK | Tower
cable ladder damage |  | CIVIL_WORK | Cable Tray
Shelter Foundation is damage (OT site and Generator Affected on foundation) |  | CIVIL_WORK | Foundation
Antennas poles/mw brackets and nut bolts rusty |  | CIVIL_WORK | Antenna Pole
BATTETIES ARE WEAK (IBS SITE Required batteries are not available) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
MW antenna's brackets and nut bolts rusty |  | CIVIL_WORK | Antenna Pole
MW antennas's brackets and nut bolts rusty |  | CIVIL_WORK | Antenna Pole
TOWER GROUNDING STOLEN |  | GROUNDING | GROUNDING
TOWER LIGHTNING PROTECTOR CABLE STOLEN |  | GROUNDING | GROUNDING
RRU's not properly not fixed/Brackets rusty |  | CIVIL_WORK | Antenna Pole
Grounding Stolen+tower lightening protection cable |  | GROUNDING | GROUNDING
CP METER BOX PARTLY DAMAGED |  | CIVIL_WORK | ACDB
Main Gate broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Climbing ladder Rusty |  | CIVIL_WORK | Cable Tray
FENCE MISSING FROM FRONT SIDE |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Metro3100 is dismental |  | EXTRA MATERIAL | EXTRA MATERIAL
Tower grounding is stolen |  | GROUNDING | GROUNDING
Tower Leg grounding is not available |  | GROUNDING | GROUNDING
INDOOR EXTRA MATERIAL(ERICSSON 3G RBS)(OSN CABINET) |  | EXTRA MATERIAL | EXTRA MATERIAL
CP METER BOX DOOR BROKEN | Power meter Box door hings/fixation required | CIVIL_WORK | ACDB
COMPOUND DAMAGED |  | CIVIL_WORK | Compound Damage
AVIATION LIGHT BOARD BURNT(FLASH TECHNOLOGY) | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION LIGHT BOARD
TOWER GOUNDING STOLEN |  | GROUNDING | GROUNDING
MAIN GROUNDING CABLE IS STOLEN |  | GROUNDING | GROUNDING
AVIATION BOARD(FLASH TECHNOLOGY) FAULTY | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
Aviation Light Board Faulty | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
Tower grounding is broken |  | GROUNDING | GROUNDING
AVIATION LIGHT BOARD FAULTY | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION LIGHT BOARD
Tower grounding is missing |  | GROUNDING | GROUNDING
TOWER leg grounding is broken & cable missing |  | GROUNDING | GROUNDING
RECTIFIER DOOR NOT INSTALLED DUE TO LOW SPACE AND WRONG INSTALLATION |  | DESIGN ISSUE | WRONG INSTALLATION
SHELTER FAUNDATION NEED REPAIR |  | CIVIL_WORK | Indoor Shelter
DELTA AC UNIT FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
cat lader damaged |  | CIVIL_WORK | Cable Tray
RT ladder is not available to reach antena, |  | DESIGN ISSUE | CIVIL_WORK
no safe ladder to reach the antena, |  | DESIGN ISSUE | CIVIL_WORK
the batteries are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
the batteries are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
no external safe ladder to reach the site |  | DESIGN ISSUE | CIVIL_WORK
the batteries are weak (no way to the site crane required to replace batteries ) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
the batteries are FAULTY | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Complete Fence / Gate / Power DB and Tower Rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
TOWER NOT SAFE TO CLIMB |  | DESIGN ISSUE | CIVIL_WORK
TOWER LEGS ARE DAMAGED |  | CIVIL_WORK | Tower
One sector is block due to construction of additional building in front |  | OTHERS | sector blockage
TOWER GROUNDING STOLEN(LIGHTNING PROTECTOR) |  | GROUNDING | GROUNDING
Room WALL CRACK need civil work |  | CIVIL_WORK | Indoor Shelter
weak batteries | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
MAIN GATE AND BOUNDRAY WALL ARE completely 'RUSTED |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main Gate Rusted |  | CIVIL_WORK | Paint Job
RRU GROUNDING CABLE NOT CONNECTED TO GROUNDING BAR |  | GROUNDING | GROUNDING
EXTRA MATERIAL AND DISMINTAL SHELTER IN COMPOUND |  | EXTRA MATERIAL | EXTRA MATERIAL
seepage of water inside room |  | CIVIL_WORK | Indoor Shelter
Main Earthwire is cutt |  | GROUNDING | GROUNDING
BATTRY WEAK WEAK | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
FENCE IS MISSING |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower & shelter outside grounding & grounding bar isstolen |  | GROUNDING | GROUNDING
need dedicated ladder for rooftop section |  | DESIGN ISSUE | CIVIL_WORK
SEEPAGE ON WALL AND GROUND AND CRACH FOUND |  | CIVIL_WORK | Indoor Shelter
LADDER NOT AVAILBLE TO REACH ANTENNA |  | DESIGN ISSUE | CIVIL_WORK
UNSAFE PATHWAY TO REACH ANTENNA,ITS SLIPPERY AND STEEP |  | DESIGN ISSUE | CIVIL_WORK
ANTENNA+RRU MOUNT POLE ASSEMBLY IS BADLY RUSTED FOR ALL SECTORS |  | CIVIL_WORK | Antenna Pole
POWER PLUG CABLES STATUS NOT OK AT WIMAX |  | OTHERS | Power connection
EMERGENCY LIGHT FULL PANEL FAULTY |  | Emergency Light | Emergency Light
OPTICAL FIBER DRESSING NOT PROPER | Fiber cables not arranged properly | CABLE DRESSING | Fiber
OMANTEL TOWER LEGS ARE RUSTED/HONEYBEED RESIDING ON TOWER |  | CIVIL_WORK | TOWER
NO PROPER ACCESS LADDER FOR ANTENNA (6M TOWER) |  | DESIGN ISSUE | CIVIL_WORK
LAND SLIDING FROM INSIDE BOUNDRY WALL,THERE IS A HOLE NEAR FENCE |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
UNSAFE WAY TO ANTENNA |  | DESIGN ISSUE | CIVIL_WORK
NO ACCESS LADDER FOR ANTENNA (RT SITE) |  | DESIGN ISSUE | CIVIL_WORK
Router Connected on AC power |  | DESIGN ISSUE | DESIGN ISSUE
FUEL SPREAD OUT ON GROUND INSIDE COMPOUND AFTER FUEL WAS THEFT |  | OTHERS | Fuel
OPTICAL FIBER DRESSING NOT PROPER | Fiber cables not arranged properly | CABLE DRESSING | Fiber
CAT/CABLE LADDER IS RUSTED |  | CIVIL_WORK | Cable Tray
Optical Fiber Dressing Not Proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Tower foundation is affected by rain. |  | CIVIL_WORK | Tower
HORIZANTAL LADDER ONLY TO REACH ROOM IN TWO FLOOR BUILDING |  | DESIGN ISSUE | CIVIL_WORK
FIBER CABLE FOR BUSNISS CUSTOMER IS NOT PROPERLY ROUTED AND PROTECTED |  | DESIGN ISSUE | Wrong Installation
PATHWAY DAMAGED(ESCALATED ON EMAIL) |  | CIVIL_WORK | PATHWAY DAMAGE
ACCESS LADDER FOR ROFTOP FROM GROUND IS BADLY RUSTED +ROOFTOP DEDICATED LADDER BROKEN |  | CIVIL_WORK | RT Ladder
RT CLIMBING LADDER IS MISSING (6M) |  | DESIGN ISSUE | CIVIL_WORK
Two TOWER leg GROUNDING STOLEN(LIGHTNING PROTECTOR) |  | GROUNDING | GROUNDING
SHELTER OD GROUNDING STOLEN(FROM BUS BAR TO EARTH PIT-5M) |  | GROUNDING | GROUNDING
Fiber cable not arrangment need CR to arrange it | Fiber cables not arranged properly | CABLE DRESSING | Fiber
ooredoo ladder door broken |  | CIVIL_WORK | RT Ladder
LADDER TO ANTENNA NOT FIXED PROBABLY |  | CIVIL_WORK | RT Ladder
COMPOUND DAMAGED |  | CIVIL_WORK | Compound Damage
ANTENNA MOUNT POLE ASSEMBLY MW IS BADLY RUSTED |  | CIVIL_WORK | Antenna Pole
FULL SHELTER BODY PAINT REQUIRED |  | CIVIL_WORK | Indoor Shelter
NO SAFE WAY RO CLIMB POLES TO CHECK UPER RRU,ABOUT 2 METER LADDER REQUIRED |  | DESIGN ISSUE | CIVIL_WORK
fiber CABLING STATUS NOT OK | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Fiber cable not arrangment need CR to arrange it | Fiber cables not arranged properly | CABLE DRESSING | Fiber
no safe ladder to reach the antenas |  | DESIGN ISSUE | CIVIL_WORK
TOWER FOUNDATION CRACKED |  | CIVIL_WORK | Tower
NPT TOWER SAFETY RAIL RUSTED |  | CIVIL_WORK | Tower
HSE ISSUE NOT SAFE.. INDOOR AC DIFFICULT TO CLEAN LIFTING MOTORE NEAR FROM ID UNIT |  | DESIGN ISSUE | CIVIL_WORK
LADDER TO ANTENNA NOT FIXED PROBABLY |  | CIVIL_WORK | RT Ladder
EMERGANCY LIGHT NOT WORKING. |  | Emergency Light | Emergency Light
Optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
no safe ladder to reach the antenas |  | DESIGN ISSUE | CIVIL_WORK
Optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
seepage and wall crack inside Room |  | CIVIL_WORK | Indoor Shelter
EMERGENCY FULL LIGHT BOARD FAULTY(SPARE MISSING IN WAREHOUSE) |  | Emergency Light | Emergency Light
OSN FIBER DRESSING & RUTTING NOT OK | Fiber cables not arranged properly | CABLE DRESSING | Fiber
TOWER MAIN GROUNDING IS MISSING(35M) |  | GROUNDING | GROUNDING
wimax antenna mount assembly is rusted completely |  | CIVIL_WORK | Antenna Pole
Optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
EMERGENCY FULL LIGHT BOARD FAULTY |  | Emergency Light | Emergency Light
No proper ladder to work at antennas |  | DESIGN ISSUE | CIVIL_WORK
no ladder to reach and work on antenna and outdoor AC (REQUIRED 3 METER) |  | DESIGN ISSUE | CIVIL_WORK
Fixed 3.5m ladder required to access to antenna,RRU |  | DESIGN ISSUE | CIVIL_WORK
OPTICAL FIBER DRESSING NOT PROPER,Fiber cable not protected | Fiber cables not arranged properly | CABLE DRESSING | Fiber
SUN SHADOW NOT AVAILABLE |  | DESIGN ISSUE | Sun Shade
No proper ladder to work at Aircons |  | DESIGN ISSUE | CIVIL_WORK
DG ALARM CABLE NEED RE-ARANGMENT UNDER GROUNND |  | DG ISSUES | DG ISSUES
DG TANK FEULE LEVEL IS NOT VESIABLE |  | DG ISSUES | DG ISSUES
SUN SHADOW NOT AVAILABLE |  | DESIGN ISSUE | Sun Shade
SUN SHADOW NOT AVAILABLE |  | DESIGN ISSUE | Sun Shade
EMERGENCY LIGHT FAULTY |  | Emergency Light | Emergency Light
Fence is broken due to land sliding, same can be repeated in future and can damage equipment |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
MAIN GATE CONCRETE COLUM IS DAMAGE(CIVIL WORK) |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
MESH WIRE ARE DAMAGED |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Trunk cable cover broken |  | CIVIL_WORK | Cable Tray
Business customer at AC power |  | DESIGN ISSUE | DESIGN ISSUE
fiber cable not properly routed | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Proper ladder not available to work at antennas |  | DESIGN ISSUE | CIVIL_WORK
Proper ladder not available to work at OUTDOOR AIRCONS |  | DESIGN ISSUE | CIVIL_WORK
Tower leg grounding is stolen |  | GROUNDING | GROUNDING
no safe ladder to reach the antenas |  | DESIGN ISSUE | CIVIL_WORK
tower lightinig arrestor rod missing |  | GROUNDING | GROUNDING
due to greater load on antenna mount pole is vibrating too much |  | CIVIL_WORK | Antenna Pole
two sectors at unsafe location mounted on outer side of building wall |  | DESIGN ISSUE | CIVIL_WORK
extra material metro in site |  | EXTRA MATERIAL | EXTRA MATERIAL
FIBER NEED ARRANGMENT | Fiber cables not arranged properly | CABLE DRESSING | Fiber
optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
NO PROPER ACCESS PATHWAY TO SITE AND ANTENNA |  | DESIGN ISSUE | CIVIL_WORK
laddeR NOT AVAILBLE TO REACH ANTENNA |  | DESIGN ISSUE | CIVIL_WORK
NO PROPER PATHWAY TO ACCESS ANTENNA |  | DESIGN ISSUE | CIVIL_WORK
optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
GATE RUSTY |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
FENCE RUSTY |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
TOWER CABLE TRAY LADDER RUSTY |  | CIVIL_WORK | Cable Tray
EARTH ROD MISSING |  | GROUNDING | GROUNDING
ROOF TOP SITE Ladder is undafe for climbing ,TO ANTENNA(ABOUT 4 METER REQUIRED) |  | DESIGN ISSUE | CIVIL_WORK
EXTRA MATERIAL METRO in site POWER ALREADY OFF |  | EXTRA MATERIAL | EXTRA MATERIAL
FIBER NEED ARRANGMENT | Fiber cables not arranged properly | CABLE DRESSING | Fiber
B.C CONNECTED TO AC POWER |  | DESIGN ISSUE | DESIGN ISSUE
laddeR NOT AVAILBLE TO REACH ANTENNA |  | DESIGN ISSUE | CIVIL_WORK
Main Groubding Cable of Antennas and RRU's Not available |  | GROUNDING | GROUNDING
Optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
laddeR NOT AVAILBLE TO REACH ANTENNA |  | DESIGN ISSUE | CIVIL_WORK
ONE TOWER GROUNDING IS STOLEN |  | GROUNDING | GROUNDING
paint needed outside Room |  | CIVIL_WORK | Paint Job
small crack at tower leg foundation |  | CIVIL_WORK | Tower
optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
FENCE BROCKEN |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
SHELTER LADDER MISSING |  | CIVIL_WORK | Indoor Shelter
FIBER NEED ARRANGMENT | Fiber cables not arranged properly | CABLE DRESSING | Fiber
CRACK FOUND ON WALL |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
CRACK FOUND ON GATE PILLAR |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
TOWER CABLE LADDER RUSTY |  | CIVIL_WORK | Cable Tray
FENCE RUSTY |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
EARTH ROD MISSING |  | GROUNDING | GROUNDING
laddeR NOT AVAILBLE TO REACH ANTENNA |  | DESIGN ISSUE | CIVIL_WORK
laddeR NOT AVAILBLE TO REACH ANTENNA |  | DESIGN ISSUE | CIVIL_WORK
tower lightening arrestor grounding cable demaged |  | GROUNDING | GROUNDING
Full ROOM seepage patches and crack found |  | CIVIL_WORK | Indoor Shelter
B.C CONNECTED TO AC POWER |  | DESIGN ISSUE | DESIGN ISSUE
TOWER LIGHTNING PROTECTING GROUNDING STOLEN |  | GROUNDING | GROUNDING
optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Clamp to climb pole is not available |  | DESIGN ISSUE | CIVIL_WORK
antenna mount pole on tower completely rusted |  | CIVIL_WORK | Antenna Pole
outdoor cable ladder is completely rusted/broken |  | CIVIL_WORK | Cable Tray
antenna mount pole assembly rusted |  | CIVIL_WORK | Antenna Pole
Two extra rectifers inside transmission shelter((Old location) Shelter with all material still available, antennas on tower as well.) |  | EXTRA MATERIAL | EXTRA MATERIAL
omantel tower ladder is not fixed from bottom |  | CIVIL_WORK | Tower
buissiness customer CONNECTED TO AC. |  | DESIGN ISSUE | DESIGN ISSUE
BATTRY BACKUP NARADA 12V190AH DIE ZERO BACKUP | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
BATTRY BACKUP NARADA 12V190AH DIE ZERO BACKUP | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
cracks in copmpound walls |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
laddeR NOT AVAILBLE TO REACH ANTENNA |  | DESIGN ISSUE | CIVIL_WORK
Weak batteries | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Delta Outdoor Ac Faulty |  | DELTA CABINET | DELTA _AIRCON FAULTY
AVIATION LIGHT FAULTY | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION LIGHT BOARD
AVIATION LIGHT FAULTY | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION LIGHT BOARD
TOWER PAINT NOT OK |  | CIVIL_WORK | Paint Job
TOWER CAT LADDER RUSTY |  | CIVIL_WORK | Tower
MAIN GATE IS RUSTY |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
no dedicated ladder for rooftop antennas |  | DESIGN ISSUE | CIVIL_WORK
BATTRY BACKUP NARADA 12V190AH DIE ZERO BACKUP | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
BATTRY BACKUP NARADA 12V190AH DIE ZERO BACKUP | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
BATTRY BACKUP NARADA 12V190AH WEAK | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
BATTRY BACKUP SHOTO 12V190AH WEAK | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
TOWER LIGHTNING PROTECTING & Equipment GROUNDING STOLEN |  | GROUNDING | GROUNDING
tower equipment grounding stolen |  | GROUNDING | GROUNDING
cracks in compound wall |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
TOWER LIGHTNING PROTECTING GROUNDING & equipment STOLEN |  | GROUNDING | GROUNDING
PATHWAY DAMAGED(ESCALATED ON EMAIL) |  | CIVIL_WORK | PATHWAY DAMAGE
CP METER DB Rusted |  | CIVIL_WORK | ACDB
Rectifier not properly fixed |  | RECTIFIER | Rectifier
TOWER LIGHTNING PROTECTING cable not availble |  | GROUNDING | GROUNDING
tower equipment grounding stolen |  | GROUNDING | GROUNDING
TOWER LIGHTNING PROTECTING cable not availble |  | GROUNDING | GROUNDING
Main Gate Rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
TOWER LIGHTNING PROTECTING cable not availble |  | GROUNDING | GROUNDING
Fire panel Faulty Mavigaurd |  | FIRE EQUIPMENT | FIRE PANEL
TOWER LIGHTNING PROTECTING cable not availble |  | GROUNDING | GROUNDING
tower equipment grounding stolen |  | GROUNDING | GROUNDING
BATTRY BACKUP SHOTO DIE ZERO BACKUP | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERIES (SHOTO-12V-100AH(4) & 1 SHOTO 12V-190AH) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
BATTERY BACKUP MEDIUM (DengTa-12V-150AH(16) |  | BATTERY BACKUP | BATTERY BACKUP
BATTERY BACK UP WEAK (Nrada-12V-190AH(8) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
NO PROPER ACCESS LADDER FOR ANTENNA (NPT TOWER) |  | DESIGN ISSUE | CIVIL_WORK
NO PROPER ACCESS LADDER FOR ANTENNA (RT SITE) |  | DESIGN ISSUE | CIVIL_WORK
TOWER LIGHTNING PROTECTING EARTH MISSING |  | GROUNDING | GROUNDING
lightening arrestor grounding cable stolenf |  | GROUNDING | GROUNDING
no dedicated ladder for rooftop antennas |  | DESIGN ISSUE | CIVIL_WORK
rooftop access ladder is rusted |  | DESIGN ISSUE | CIVIL_WORK
rectifier controller display is faulty |  | RECTIFIER | huawei ETP48300 Display
laddeR NOT AVAILBLE TO REACH ANTENNA |  | DESIGN ISSUE | CIVIL_WORK
POWER CABLE ROUTING NOT PROPER | Main Power Cables not arranged properly | CABLE DRESSING | Power Cable
main Grounding stolen for outdoor equipment |  | GROUNDING | GROUNDING
4 batteries weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
main Grounding stolen for outdoor equipment |  | GROUNDING | GROUNDING
tower equipment grounding stolen |  | GROUNDING | GROUNDING
NOT SAFE LADDER AVAILABLE FOR CLIMBING (4M) |  | DESIGN ISSUE | CIVIL_WORK
BATTERY BACK UP WEAK (Nrada-12V-190AH(8) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Monopole tower ladder unsafe for climbing (30 m) |  | DESIGN ISSUE | CIVIL_WORK
Gate fence is broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
TOWER NOT SAFE TO CLIMB (MOD tower) |  | CIVIL_WORK | Tower
omantel fence is broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site fence is demaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Antenna Mount Poles, CP BOx and Cat ladder is damage due to Rust |  | CIVIL_WORK | Antenna Pole
FENCE IS BROKEN AND FENCE SUPPORT RODS ARE RUSTED |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fence not avaliable |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
POWER CABLE ROUTING NOT PROPER | Main Power Cables not arranged properly | CABLE DRESSING | Power Cable
Main Gate Rusted |  | CIVIL_WORK | Paint Job
optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
delta DOOR handle FAULTY |  | DELTA CABINET | Door LOCK
Main DB damaged |  | CIVIL_WORK | ACDB
weak batteries | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
FIBER WORK NOT DONE PROPERLY | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Many snags Open site still not acceptedUnder of project team |  | CIVIL_WORK | OTHERS
Main access ladder rusted (25 m) |  | CIVIL_WORK | Tower
NOT SAFE LADDER AVAILABLE FOR CLIMBING (5M) |  | DESIGN ISSUE | CIVIL_WORK
NOT SAFE LADDER AVAILABLE FOR CLIMBING (5M) |  | DESIGN ISSUE | CIVIL_WORK
FIBER WORK NOT DONE PROPERLY & ODF INSTALLED INSIDE OMANTEL SHELTER | Fiber cables not arranged properly | CABLE DRESSING | Fiber
NO PATHWAY TO ACCESS SITE |  | CIVIL_WORK | PATHWAY DAMAGE
AMP 30 SUN SHADE IS DAMAGE |  | DESIGN ISSUE | Sun Shade
NO PROPER ACCESS LADDER FOR ANTENNA (RT SITE) |  | DESIGN ISSUE | CIVIL_WORK
Tower leg grounding is broken |  | GROUNDING | GROUNDING
EXTRA MATERIAL IN SHELTER (DPD63-8-8 RECTIFIER |  | EXTRA MATERIAL | EXTRA MATERIAL
NOT SAFE LADDER AVAILABLE FOR CLIMBING RT POLE(Antenna) (4M) |  | DESIGN ISSUE | CIVIL_WORK
BATTERY BANK 1 WEAK | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
NOT SAFE LADDER AVAILABLE FOR CLIMBING RT POLE(Antenna) (4M) |  | DESIGN ISSUE | CIVIL_WORK
SUN SHADOW COVER NOT AVAILABLE |  | DESIGN ISSUE | Sun Shade
SUN SHADOW COVER NOT AVAILABLE |  | DESIGN ISSUE | Sun Shade
BATTERY BACK UP MEDIUM (12V-190AH(8) |  | BATTERY BACKUP | BATTERY BACKUP
NOT SAFE LADDER AVAILABLE FOR CLIMBING RT POLE(Antenna) (4M) |  | DESIGN ISSUE | CIVIL_WORK
ODF Optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
BATTERY BACK UP MEDIUM ONE BANK IS FAULTY (SHOTO-12V-180AH(4) |  | BATTERY BACKUP | BATTERY BACKUP
delta DOOR handle FAULTY |  | DELTA CABINET | Door LOCK
optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
One weak battery dengta 12/150 | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
seepage & crack inside room |  | CIVIL_WORK | Indoor Shelter
Tower Groundinf Stolen |  | GROUNDING | GROUNDING
Shelter is rusty |  | CIVIL_WORK | Indoor Shelter
Fence damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower ladder base is not properly fixed |  | CIVIL_WORK | Foundation
Shelter is rusty |  | CIVIL_WORK | Indoor Shelter
NO PROPER ACCESS LADDER FOR ANTENNA (RT SITE) |  | DESIGN ISSUE | CIVIL_WORK
NO PROPER ACCESS LADDER FOR ANTENNA (RT SITE) |  | DESIGN ISSUE | CIVIL_WORK
LADDER TO ANTENNA NOT FIXED PROBABLY(4M) |  | CIVIL_WORK | RT Ladder
8 NRADA 12V-190AH BATTERIES FAULTY |  | BATTERY BACKUP | BATTERY BACKUP
BATTERIES FAULTY 3 (SHOTO-12V-180AH) | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Safe ladder not available to reach at antennas |  | DESIGN ISSUE | CIVIL_WORK
Safe ladder not available to reach at antennas |  | DESIGN ISSUE | CIVIL_WORK
One weak battery dengta 12/150 | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Main DB cover damaged |  | CIVIL_WORK | ACDB
weak batteries needed to replace | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
One weak battery dengta 12/150 | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
2 batteries weak dengta 12/150 | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fence damaged from top sides |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
weak batteries dengta 12/150 | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
ONE BATTERY IS FAULTY (DengTa-12V-150AH) | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
ONE BATTERY IS FAULTY (DengTa-12V-150AH) | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
TWO BATTERY IS FAULTY (DengTa-12V-150AH) | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
TWO BATTERY IS FAULTY (DengTa-12V-150AH) | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
BATTRIES ARE WEAK NRADA 12V-190AH (8) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Outdoor Delta AC is faulty (EX-E02 C)( HUAWEI DELTA ) |  | DELTA CABINET | DELTA _AIRCON FAULTY
Outdoor Delta AC is faulty (EX-E02 C)( HUAWEI DELTA ) |  | DELTA CABINET | DELTA _AIRCON FAULTY
BATTERY BACK UP WEAK (DengTa-12V-150AH 6 BATTERIES FAULTY | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
B.C.CONNECTED TO AC. |  | DESIGN ISSUE | DESIGN ISSUE
Shelter door step damage |  | CIVIL_WORK | Indoor Shelter
OSN Shelter leakage |  | CIVIL_WORK | Indoor Shelter
Main tower grounding stolen from tower to main earth pit |  | GROUNDING | GROUNDING
APM30 battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
POWER METER BOX/Eath Bit Grounding cover NEED TO REPLACE | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
Alarms not reporting because of NPU not compatible |  | OTHERS | EXTERNAL ALARMS
Tower legs grounding are missing |  | GROUNDING | GROUNDING
lightening arrestor grounding strip is broken on tower |  | GROUNDING | GROUNDING
no dedicated ladder for rooftop antennas |  | DESIGN ISSUE | CIVIL_WORK
Feeder Tray rusty |  | CIVIL_WORK | Cable Tray
Sand inside compound |  | CIVIL_WORK | Compound Damage
Tower foundation have cracks |  | CIVIL_WORK | Tower
Tower rusty |  | CIVIL_WORK | Tower
main Grounding stolen from shelter to pain bar |  | GROUNDING | GROUNDING
Sand inside compound |  | CIVIL_WORK | Sand
All site fence Damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra material at site |  | EXTRA MATERIAL | EXTRA MATERIAL
CAT ladder is rusted and broken Need to Replace |  | CIVIL_WORK | RT Ladder
no dedicated ladder for rooftop antennas |  | DESIGN ISSUE | CIVIL_WORK
4-BATTERIES FAULTY (DengTa-12V-150AH) | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
BATTERY BACK UP WEAK (Nrada-12V-190AH(8) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
RECTIFIER-2 BATTERY BACK UP WEAK (NORTH STAR-12V-100AH(4) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
NOT SAFE LADDER AVAILABLE FOR CLIMBING (5M) |  | DESIGN ISSUE | CIVIL_WORK
NOT SAFE LADDER AVAILABLE FOR CLIMBING (5M) |  | DESIGN ISSUE | CIVIL_WORK
BATTERY BACK UP MEDIUM (DengTa-12V-150AH(12) batteries faulty |  | BATTERY BACKUP | BATTERY BACKUP
BOUNDARY FENCE RUSTED & DOOR DAMAGED |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
seepage & crack inside room |  | CIVIL_WORK | Paint Job
4 weak batteries Dengta 12/150 AH | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
weak batteries | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
all sectors main grounding stolen |  | GROUNDING | GROUNDING
3 batteries weak dengta 12/150 | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
4 batteries of APM30 weak 12/100 | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
main grounding stolen |  | GROUNDING | GROUNDING
16 BATTRY BACKUP DENGTA 12V150AH WEAK IN APM RECTIFIER | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
VSAT MODEM NOT MOUNTED |  | OTHERS | OTHERS
TOWER NOT SAFE TO CLIMB (NO LADDER AVAIABLE ON TOWER-5M) |  | DESIGN ISSUE | UNSAFE LADDER
NO PROPER ACCESS LADDER FOR ANTENNA (RT SITE) |  | DESIGN ISSUE | CIVIL_WORK
Main Grounding Cable Not Available |  | GROUNDING | GROUNDING
Delta AC (1) IS FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
Batteries is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Huawei APM30H (WIMAX) Battreis weak (12v,92ah) | TDD/WiMax Battery Backup is Weak | BATTERY BACKUP | BATTERY BACKUP
Batteries is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Huawei Delta Aircon Faulty |  | DELTA CABINET | DELTA _AIRCON FAULTY
BATTERIES FAULTY 4 NARADA 12V0190AH | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
NOT SAFE LADDER AVAILABLE FOR CLIMBING (5M) RT |  | DESIGN ISSUE | CIVIL_WORK
two batteries weak 12/150 dengta | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Batteries of same ratings must be used in rectifier |  | BATTERY BACKUP | BATTERY BACKUP
three batteries weak 12/150 dengta | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
tower lightening arrestor grounding cable stolen |  | GROUNDING | GROUNDING
tower lightening arrestor grounding metal strip broken |  | GROUNDING | GROUNDING
RF ANTENNA MOUNT POLE CEMENTED FOUNDATION.IS DAMAGED |  | CIVIL_WORK | Antenna Pole
SABCO FM EQUIPMENT ON AC SUPPLY |  | DESIGN ISSUE | DESIGN ISSUE
SHELTER ID EMERGECY LIGHT FAULTY |  | Emergency Light | Emergency Light
SHELTER OUTDOOR GROUNDING CABLE STOLEN(FROM BUS BAR TO EARTH PIT) |  | GROUNDING | GROUNDING
SHELTER OD LIGHT HOLDER BROKEN |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
SHELTER OUTDOOR GROUNDING CABLE STOLEN(FROM BUS BAR TO EARTH PIT) |  | GROUNDING | GROUNDING
AVIATION LIGHT BOARD FAULTY(FLASH TECHNOLOGY) | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION LIGHT BOARD
weak batteries need to replace Narada 12/190 | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
delta DOOR handle FAULTY |  | DELTA CABINET | Door LOCK
lightening protection cable stolen |  | GROUNDING | GROUNDING
weak batteries dengta 12/150 | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
weak batteries needed to replace | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
weak batteries Shoto 12/180 | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Both Microwave Antenna Face is damaged |  | OTHERS | Microwave Antenna
Tower Base and Vsat Dish base is affected by rain |  | CIVIL_WORK | Tower
NO PROPER ACCESS LADDER FOR ANTENNA (RT SITE) |  | DESIGN ISSUE | CIVIL_WORK
TOWER GROUNDING STOLEN(LIGHTNING PROTECTOR) |  | GROUNDING | GROUNDING
TOWER MAIN GROUNDING MISSING |  | GROUNDING | GROUNDING
Door lock is broken |  | CIVIL_WORK | Indoor Shelter
GATE NOT OK |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
TOWER FOUNDATION STATUS NOT OK |  | CIVIL_WORK | Tower
TOWER GROUNDING STOLEN(FROM MINI BUS BAR AND LIGHTNING PROTECTOR) |  | GROUNDING | GROUNDING
TOWER LIGHTNING PROTECTING GROUNDING STOLEN |  | GROUNDING | GROUNDING
batteries backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Wimax Batteries backup weak | TDD/WiMax Battery Backup is Weak | BATTERY BACKUP | BATTERY BACKUP
batteries backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
batteries backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Monopole tower ladder unsafe for climbing (30 m) |  | DESIGN ISSUE | CIVIL_WORK
NOT SAFE LADDER AVAILABLE FOR CLIMBING (5M) |  | DESIGN ISSUE | CIVIL_WORK
TN-BATTERY BACK UP WEAK (North star-12V-100AH(4) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WIMAX-BATTERY BACK UP WEAK (DengTa-12V-92AH(8) | TDD/WiMax Battery Backup is Weak | BATTERY BACKUP | BATTERY BACKUP
SHELTER DOOR IS DAMAGED |  | CIVIL_WORK | Indoor Shelter
6 Cell NARAD12V/190AH | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
TOWER PAINT REQUIRED |  | CIVIL_WORK | Paint Job
DELTA HANDEL IS FAULTY |  | DELTA CABINET | Door LOCK
4 Cell SHOTO 12V/100AH FAIL IN APM RECTFIER |  | BATTERY BACKUP | BATTERY BACKUP
5 Cell SHOTO 12V/100AH LOW BACKUP | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Bus bar missing |  | GROUNDING | GROUNDING
Tower rod grounding cable is missing |  | GROUNDING | GROUNDING
TOWER LIGHTNING PROTECTOR GROUNDING STOLEN(35M) |  | GROUNDING | GROUNDING
TOWER LIGHTNING PROTECTOR GROUNDING STOLEN(50M) |  | GROUNDING | GROUNDING
Main meter cover is broken | Power meter Box door hings/fixation required | CIVIL_WORK | ACDB
Extra material at shelter no 2 (Cables and Fibres) |  | EXTRA MATERIAL | EXTRA MATERIAL
1 BATTERY BANK MISSING(SHOTO 12V 190AH) |  | BATTERY BACKUP | BATTERY BACKUP
NO PROPER PATHWAY TO ACCESS TOWER (HILLTOP SITE) |  | DESIGN ISSUE | CIVIL_WORK
Sand inside compound |  | HOUSEKEEPING | HOUSEKEEPING/Omantel
Tower grounding missing |  | GROUNDING | GROUNDING
Fence broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Gate rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
5 Cell DENGTA 12V/150AH FAIL IN TEAT | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
8 Cell shoto 12V/180AH FAIL IN TEST | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Batteris backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
NOT SAFE LADDER AVAILABLE FOR AIRCON SERVICE (5M) |  | DESIGN ISSUE | CIVIL_WORK
Wall crack inside Equipment Room |  | CIVIL_WORK | Indoor Shelter
ACDB BOX UNABLE TO CLOSE DUE TO WRONG INSTALLATION |  | DESIGN ISSUE | DESIGN ISSUE
FACP BATTERY FAULTY(GENT) |  | FIRE EQUIPMENT | FACP BATTERY
Alarms labeling and configuration is not done by project team |  | DESIGN ISSUE | DESIGN ISSUE
Site is covered with sand |  | CIVIL_WORK | Compound Damage
VSAT BUC ON AC SUPPLY |  | DESIGN ISSUE | DESIGN ISSUE
Fence damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower foundation cracked |  | CIVIL_WORK | Tower
Fence damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower foundation cracked |  | CIVIL_WORK | Tower
Fence damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Earthing pit is not available |  | GROUNDING | GROUNDING
Earthing pit is not available |  | GROUNDING | GROUNDING
TOWER LIGHTNING PROTECTOR GROUNDING STOLEN |  | GROUNDING | GROUNDING
AC SPD FAULTY (L&A LA-MP40) | 1 AC SPD FAULTY | BREAKER/RELAY/SENSOR | AC SPD FAULTY
Main Gate and Tower is rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
BATTERY BACKUP IS WEAK & NEED TO CHANGE(SHOTO) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Sand Inside Compound |  | CIVIL_WORK | Compound Damage
TOWER GROUNDING STOLEN-LIGHTNING PROTECTOR-45M |  | GROUNDING | GROUNDING
1 BB IS WEAK(SHOTO 92AH) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Tower base has cracks |  | CIVIL_WORK | Tower
Main tower grounding not ok |  | GROUNDING | GROUNDING
cable leader broken and rusted. |  | CIVIL_WORK | Cable Tray
VSAT dish supporting roads damaged and rusted |  | OTHERS | VSAT
Tower Base Rusted |  | CIVIL_WORK | Tower
TOWER GROUNDING STOLEN-LIGHTNING PROTECTOR-30M |  | GROUNDING | GROUNDING
WALL STATUS NOK(SMALL PATCH BROKEN) |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
TOWER NOT SAFE TO CLIMB(MONO POLE, DESIGN ISSUE) |  | DESIGN ISSUE | CIVIL_WORK
TOWER GROUNDING STOLEN-BUS BAR NOT CONNECTED TO EACH OTHER AND TO EARTHPIT-LIGHTNING PROTECTOR-20M |  | GROUNDING | GROUNDING
BATTRY BANK IS WEAK all battery | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DELTA HANDEL IS FAULTY |  | DELTA CABINET | Door LOCK
Outdoor Delta AC is faulty (E06-E07)( HUAWEI DELTA ) |  | DELTA CABINET | DELTA _AIRCON FAULTY
ROOF TOP LADDER NOT AVAILABLE(5M) |  | DESIGN ISSUE | CIVIL_WORK
HUAWEI DELTA CABINET AC FAULTY (EX-E02) |  | DELTA CABINET | DELTA _AIRCON FAULTY
HUAWEI DELTA CABINET AC FAULTY (EX-E02) |  | DELTA CABINET | DELTA _AIRCON FAULTY
Tower Grounding Stollen |  | GROUNDING | GROUNDING
tower grounding stolen |  | GROUNDING | GROUNDING
delta ac faulty |  | DELTA CABINET | DELTA _AIRCON FAULTY
BATTERY BACKUP IS WEAK | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DELTA AC UNIT FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
BATTRY BANK IS WEAK all battery | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
ROOM LOCK FAULTY |  | CIVIL_WORK | OTHERS
Tower Grounding Stolen |  | GROUNDING | GROUNDING
Tower Grounding Stolen |  | GROUNDING | GROUNDING
optical fiber dressing not proper | Fiber cables not arranged properly | CABLE DRESSING | Fiber
BATTRY BACKUP IN TP DENGTA 12V150AH |  | BATTERY BACKUP | BATTERY BACKUP
BATTRY BANK 3,4 IN TP DENGTA 12V150AH BATTERY |  | BATTERY BACKUP | BATTERY BACKUP
NO LADDER AVAILABLE FOR OUTDOOR AC SERVICE (4 METER REQUIRED) |  | DESIGN ISSUE | CIVIL_WORK
NO LADDER AVAILABLE FOR OUTDOOR AC SERVICE (4 METER REQUIRED) |  | DESIGN ISSUE | CIVIL_WORK
NOT SAFE LADDER AVAILABLE FOR ANTENNA (5M) |  | DESIGN ISSUE | CIVIL_WORK
NOT SAFE FOR CLIMBING RT POLE(Antenna) (3M) |  | DESIGN ISSUE | CIVIL_WORK
HSE access issue verical ladder only to access site |  | DESIGN ISSUE | CIVIL_WORK
ACCESS LOCK IS MISSING (SPARE MISSING IN WH) | Site main gate padlock is missing | PADLOCK | PADLOCK
ACCESS LOCK IS FAULTY (SPARE MISSING IN WH) | Site main gate padlock is missing | PADLOCK | PADLOCK
Fence is broken in one side |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower foundation cracked |  | CIVIL_WORK | Tower
No Fence or Gate Available At site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Indoor shelter cable ducting melted /molded due to high temprature ( need to replace ). |  | CIVIL_WORK | Cable Tray
Door lock latches required ( close door with PAD lock ) |  | CIVIL_WORK | OTHERS
Path way damage |  | CIVIL_WORK | PATHWAY DAMAGE
EXTRA MATERIAL DISMANTLE ATLAS DG/TANK AT SITE |  | EXTRA MATERIAL | EXTRA MATERIAL
DELTA handel IS FAULTY |  | DELTA CABINET | Door LOCK
TOWER PAINT NOT OK |  | CIVIL_WORK | Paint Job
CLU CABINET AND ATS PANEL SUN SHADE conopy RUSTED |  | CIVIL_WORK | CIVIL_WORK
Standby DG is not connected with OSN shelter, |  | DG ISSUES | DG ISSUES
SABCO CABINET WORKING ON AC SUPPLY |  | DESIGN ISSUE | DESIGN ISSUE
1 CELL IS FAULTY (SHOTO 12V 180AH) |  | BATTERY BACKUP | BATTERY BACKUP
GROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR-35M) |  | GROUNDING | GROUNDING
FOC is not properly routed in OSN rack | FOC Cable not arranged properly | CABLE DRESSING | CABLE DRESSING
no dedicated ladder for rooftop antennas |  | DESIGN ISSUE | CIVIL_WORK
tower foundation damaged |  | CIVIL_WORK | Tower
tower lightening arrestor grounding strip broken |  | GROUNDING | GROUNDING
cable ldder is installed on top ofoutdoor grounding plate. |  | DESIGN ISSUE | DESIGN ISSUE
SITE FENCE IS RUSTED |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site fence mesh damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower leg foundation have some cracks |  | CIVIL_WORK | Tower
site boundry wall is cracked |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
FOC not properly arranged in OSN | FOC Cable not arranged properly | CABLE DRESSING | CABLE DRESSING
tower lightening arrestor damaged |  | GROUNDING | GROUNDING
site compound level is damaged by rain water. |  | CIVIL_WORK | Compound Damage
5 batteries are faulty(12V/190Ah) | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
CP METER BOX DOOR HINGE BROKEN | Power meter Box door hings/fixation required | CIVIL_WORK | ACDB
Fence height is very small , not protected the site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower foundation cracked minorly |  | CIVIL_WORK | Foundation
outdoor sheleter , shed broken |  | CIVIL_WORK | CIVIL_WORK
Main door lock not in level , door cannt close properly , lock with Chain |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Complete Tower Grounding Missing |  | GROUNDING | GROUNDING
Main tower grounding not ok |  | GROUNDING | GROUNDING
Tower base has cracks |  | CIVIL_WORK | Tower
V-SAT Dish not fixed at concret PAD |  | DESIGN ISSUE | DESIGN ISSUE
TOWER GROUNDING CABLE STOLEN CONNECTING BOTH BUS BAR-15M |  | GROUNDING | GROUNDING
2 BATTERY BANKS MISSING HENCE ALARM ON RECTIFER |  | BATTERY BACKUP | BATTERY BACKUP
CAT LADDER STATUS NOT OK |  | CIVIL_WORK | Cable Tray
outdoor cabinet cemented foundation unbalanced due to rain water. |  | CIVIL_WORK | Foundation
L800 combiner installed on top AIRCON indoor unit |  | DESIGN ISSUE | wrong installation
ACDB cover is broken. | Power meter Box door hings/fixation required | CIVIL_WORK | ACDB
fence is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site main gate angles are damaged/broken,rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Gate base foundation is effected by rain |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shleter is rusty and stairs not available |  | CIVIL_WORK | Indoor Shelter
Tower leg grounding is stolen |  | GROUNDING | GROUNDING
LAN SWITCH WORKING ON AC SUPPPLY |  | DESIGN ISSUE | DESIGN ISSUE
CP METER BOX DOOR HINGES BROKEN | Power meter Box door hings/fixation required | CIVIL_WORK | ACDB
site compound is damaged at one corner |  | CIVIL_WORK | Compound Damage
sector C view is blocked by new building |  | OTHERS | OTHERS
outdoor cabinet foundation unbalanced due to rain water |  | CIVIL_WORK | Foundation
FOC not properly routed at TN and OSN | FOC Cable not arranged properly | CABLE DRESSING | CABLE DRESSING
wimax antenna mount pole clamps are rusted |  | CIVIL_WORK | Antenna Pole
site fence broken/fence supporting rods are rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
CP meter box completely damaged |  | CIVIL_WORK | ACDB
BOUNDRY WALL CRACKED |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site main gate is not closing properly |  | CIVIL_WORK | OTHERS
BATTERY BACKUP IS WEAK & NEED TO CHANGE | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Rectifire-2 Emerson 4 batteries faulty(12v062ah) |  | BATTERY BACKUP | BATTERY BACKUP
Seepage & crack inside room |  | CIVIL_WORK | Paint Job
Tower base has crack |  | CIVIL_WORK | Tower
fence broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site main gate rusted (need repainting) |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
tower leg grounding missing |  | GROUNDING | GROUNDING
Outdoor old delta AC FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
EXTRA MATRIAL INSIDE THE SITE ( OMAN TEL ) |  | EXTRA MATERIAL | EXTRA MATERIAL
Omantel . fence broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
GATE RUSTY |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
4 CELLS FAULTY IN BB2(SHOTO 12V 180AH) |  | BATTERY BACKUP | BATTERY BACKUP
AVIATION LIGHT BOARD FAULTY(FLASH TECHNOLOGY) | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION LIGHT BOARD
TOWER LIGHTNING PROTECTOR ROD AND GROUNDING CABLE STOLEN-10M |  | GROUNDING | GROUNDING
TOWER LIGHTNING PROTECTOR GROUNDING CABLE STOLEN-10M |  | GROUNDING | GROUNDING
DELTA AC UNIT FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
Complete Site Foundation Damage |  | CIVIL_WORK | Compound Damage
no fence or boundary wall |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
4 Batteries faulty | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
miising tower leg grounding |  | GROUNDING | GROUNDING
tower need paint |  | CIVIL_WORK | Paint Job
Fence broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
EXTRA MATERIAL |  | EXTRA MATERIAL | EXTRA MATERIAL
EXTRA MATERIAL(DISMANTLED SHELTER AS SITE SHIFTED TO HYBRID DG) |  | EXTRA MATERIAL | EXTRA MATERIAL
AVIATION LIGHT BOARD FAULTY(OPTIMA) | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
WRONG INSTALLATION(BTS AND TN INSTALLED IN WRONG CABINET HAVING NO AC, NO SENSORS, NO ALARMS PATCHED |  | DESIGN ISSUE | Design Issue
TOWER PAINT NOT OK |  | CIVIL_WORK | Paint Job
AVIATION LIGHT BOARD FAULTY(OPTIMA) | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
Rusted ladder unsafe to climb |  | CIVIL_WORK | Cable Tray
BATTERY BACKUP IS WEAK SHOTO 12V-190AH 3 BATTERIES FAULTY | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
BATTERY BACKUP IS WEAK SHOTO 12V-180AH (8) BATTERIES FAULTY | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fence broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
tower grounding stolen |  | GROUNDING | GROUNDING
WEAK BATTERY BACKUP(SHOTO 180AH)8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
AVIATION LIGHT BOARD FAULTY(OPTIMA) | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
GATE NOT BALANCED |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
NO ACCESS LADDER FOR ANTENNA (RT SITE) |  | DESIGN ISSUE | DESIGN ISSUE
FIBER NOT PROTECTED FROM OSN TO TN | Fiber cable are not secured. | CABLE DRESSING | Fiber
WEAK BATTERY BACKUP(SHOTO 180AH)8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Aviation light system is not working | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
OPTICAL FIBER DRESSING NOT PROPER(SHELTER 2 | Fiber cables not arranged properly | CABLE DRESSING | Fiber
OPTICAL FIBER DRESSING NOT PROPER | Fiber cables not arranged properly | CABLE DRESSING | Fiber
tower lightening arrestor grounding strip broken |  | GROUNDING | GROUNDING
site fence is rusted need to repaint |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site main gate angles are rusted and partly damaged+repaint required |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
LTE-TDD battery backup is zero |  | BATTERY BACKUP | BATTERY BACKUP
omantel owned site boundary wall broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
shelter frame foundation damaged |  | CIVIL_WORK | Indoor Shelter
tower leg grounding is damaged |  | GROUNDING | GROUNDING
tower leg foundation have some cracks |  | CIVIL_WORK | Tower
ACDB cover is missing |  | CIVIL_WORK | OTHERS
omantel owned tower leg foundation cracked |  | CIVIL_WORK | Tower
tower lightening arrestor is missing |  | GROUNDING | GROUNDING
site main gate repaint required |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site main gate is completely rusted. All angles are broken.requires major civil work |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
tower repaint required |  | CIVIL_WORK | Tower
oamantel owned site boundry wall cracked |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
APM30 batteries are faulty |  | BATTERY BACKUP | BATTERY BACKUP
omantel owned tower ladder is rusted |  | CIVIL_WORK | Ladder Broken
compound around tower legs damaged severely by rain water |  | CIVIL_WORK | Compound Damage
site main gate needs to paint |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
delta cabinet foundation/surface below foundation damaged by flood water |  | CIVIL_WORK | Compound Damage
tower lightening arrestor grounding cable stolen-25 m |  | GROUNDING | GROUNDING
site compound is damaged by rain water |  | CIVIL_WORK | Compound Damage
pathway is damaged .having large stones and surface is not plane |  | CIVIL_WORK | PATHWAY DAMAGE
Shelter repaint required |  | CIVIL_WORK | Indoor Shelter
site main gate fence mesh angles are broken. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
tower lightening arrestor grounding cable stolen |  | GROUNDING | GROUNDING
site main gate and fence to paint |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
tower repaint required |  | CIVIL_WORK | Tower
tower lightening arrestor missing |  | GROUNDING | GROUNDING
cable ladder support foundation not properly fixed on ground |  | CIVIL_WORK | Cable Tray
Tower leg foundation have some cracks |  | CIVIL_WORK | Tower
tower lightening arrestor ground strip broken |  | GROUNDING | GROUNDING
DG external fuel tank reapint required |  | DG ISSUES | DG ISSUES
Complete Site fence is ruested and Complete tower required paint |  | CIVIL_WORK | Tower
tower repaint required |  | CIVIL_WORK | Tower
OT Tower ladder Not comblete from down side |  | CIVIL_WORK | Ladder Broken
huawei rectifier module faulty |  | RECTIFIER | RECTIFIER MODULE
2 batteries are faulty(12V/190Ah) | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
Rectifier cabinet door lock is broken |  | OTHERS | DOOR LOCK
Dengta, 150Ah NOK | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
DengTa -12V-150AH BATTERIES FAULTY | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
One shelter at site |  | EXTRA MATERIAL | EXTRA MATERIAL
fuel pipe has leakage |  | DG ISSUES | DG ISSUES
Fuel Tank Status not ok |  | DG ISSUES | DG ISSUES
RRU mount pole clamps are rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main gate damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
DG battery Faulty |  | DG ISSUES | DG ISSUES
All Batteries Are Fault (Shoto 190Ah) | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
LOGOTIMER NOT SUPPORTED BY AIRCON DB | LOGOTIMER NOT SUPPORTED BY AIRCON DB | AIR_CONDITIONER | LOGO TIMER
FIBER NOT PROTECTED FROM ODF TO OSN | Fiber cable are not secured. | CABLE DRESSING | Fiber
ETHERNET CABLE NOT ROUTED PROPERLY FROM SHELTER TO OD APM | OD cable not arranged properly | CABLE DRESSING | CABLE DRESSING
BB IS WEAK(SHOTO 190AH) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
All Batteries are Faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
1 CELL IS WEAK 190AH | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
FENCE BROKEN |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
TOWER LIGHTNING PROTECTOR ROD GROUNDING CABLE STOLEN-30M |  | GROUNDING | GROUNDING
Tower Grounding Stolen (Leg). |  | GROUNDING | GROUNDING
The main gate floor has deteriorated slightly due to the rain. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
The main gate floor has deteriorated slighty due to rain |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Huawei Outdoor cabinet door Lock damaged due to couldn’t Lock the door. |  | OTHERS | DOOR LOCK
Gravel floor has damaged near the wall due to rain and has become a pit. |  | CIVIL_WORK | Compound Damage
Optima AC tower Light Faulty | Aviation light (Bulb) Faulty/damaged | AVIATION_LIGHT | Tower Light
Boundry wall has a crack. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
AC1 COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | A/C COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | AIR_CONDITIONER | Compressor
BATTERIES STOLEN- 8 CELLS | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
BATTERIES STOLEN- 8 CELLS | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Tower is rusty, Lot of garbage at site (Omantell Site) |  | CIVIL_WORK | Tower
Boundry wall has multiple cracks. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
WEAK BATTERY BACKUP | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
FENCE BROKEN |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
FENCE BROKEN |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
SHELTER ID EMERGENCY LIGHT SET FAULTY |  | Emergency Light | Emergency Light
LOGOTIMER NOT SUPPORTED BY AIRCON DB | LOGOTIMER NOT SUPPORTED BY AIRCON DB | AIR_CONDITIONER | LOGO TIMER
WEAK BATTERY BACKUP (180AH) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Main Gate and complete fence damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Earthing Pit not available |  | GROUNDING | GROUNDING
LOGOTIMER NOT SUPPORTED BY AIRCON DB | LOGOTIMER NOT SUPPORTED BY AIRCON DB | AIR_CONDITIONER | LOGO TIMER
LOGOTIMER NOT SUPPORTED BY AIRCON DB | LOGOTIMER NOT SUPPORTED BY AIRCON DB | AIR_CONDITIONER | LOGO TIMER
SHELTER LADDER MISSING |  | CIVIL_WORK | Indoor Shelter
SHELTER LADDER MISSING |  | CIVIL_WORK | Indoor Shelter
.Cp power meter base damage | Power meter Box and bases completely rusty-Damaged | CIVIL_WORK | ACDB
Tower aviation light Board faulty | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
Fence Damage (omantel as Host) |  | CIVIL_WORK | CIVIL_WORK
Need refilling concrete inside boundary |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fence Damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fence is Damaged and rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
SDG need to service and paint |  | DG ISSUES | DG ISSUES
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup weak rectifire 3 ericsson pbc6500 | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Earthing pit Cover Broken |  | GROUNDING | GROUNDING
CP METER BOX DOOR BROKEN | Power meter Box door hings/fixation required | CIVIL_WORK | ACDB
TOWER ROD GROUNDING CABLE STOLEN-LIGHTNING PROTECTOR-30M |  | GROUNDING | GROUNDING
TOWER GROUNDING CABLE STOLEN (LIGHTNING PROTECTOR AND BETWEEN BUS BAR) |  | GROUNDING | GROUNDING
TOWER CABLE TRAY LADDER STATUS NOT OK |  | CIVIL_WORK | Cable Tray
FENCE BROKEN |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
NO PROPER ACCESS PATHWAY TO SITE |  | DESIGN ISSUE | CIVIL_WORK
NO PROPER ACCESS PATHWAY TO SITE |  | DESIGN ISSUE | CIVIL_WORK
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
ODF Box not properly fixed | OD cable not arranged properly | CABLE DRESSING | CABLE DRESSING
Battery backup weak & Two bank missing | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup weak & Two bank missing | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Outdoor Delta AC is faulty (EX-E02 C)( HUAWEI DELTA ) |  | DELTA CABINET | DELTA _AIRCON FAULTY
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Rectifire-02 Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
ROOF TOP LADDER MISSING FOR OUTDOOR AC(4M) |  | DESIGN ISSUE | CIVIL_WORK
Battery backup weak & one bank missing(DengTa 12v0150ah) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup weak (all batteries missing) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Outdoor Delta AC is faulty (EX-E02 C)( HUAWEI DELTA ) |  | DELTA CABINET | DELTA _AIRCON FAULTY
Outdoor Delta AC is faulty (EX-E02 C)( HUAWEI DELTA ) |  | DELTA CABINET | DELTA _AIRCON FAULTY
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Outdoor Delta AC is faulty (EX-E02 C)( HUAWEI DELTA ) |  | DELTA CABINET | DELTA _AIRCON FAULTY
Outdoor Delta AC is faulty (EX-E02 C)( HUAWEI DELTA ) |  | DELTA CABINET | DELTA _AIRCON FAULTY
Thorny Bush cut needed with Special Machine | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Main gate rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
All batteries missing (Zero backup) | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Battery one bank is missing 12v-150ah | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
LOGOTIMER FAULTY | A/C LOGOTIMER FAULTY | AIR_CONDITIONER | LOGO TIMER
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Outdoor Delta AC is faulty (EX-E02 C)( HUAWEI DELTA ) |  | DELTA CABINET | DELTA _AIRCON FAULTY
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
All batteries missing (Zero backup) | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
LOGOTIMER FAULTY | A/C LOGOTIMER FAULTY | AIR_CONDITIONER | LOGO TIMER
HSE issue accessing AC OD units |  | DESIGN ISSUE | Design Issue
Improper Power cables routing | Main Power Cables not arranged properly | CABLE DRESSING | Power Cable
batteries Fault | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Smoke Sensor Not Available |  | OTHERS | Smoke Sensor
Shelter 2, FP Faulty |  | FIRE EQUIPMENT | FIRE PANEL
WRONG INSTALLATION OF AVR(BLOCKING AC1 IDU AND AIRCON DB) |  | DESIGN ISSUE | DESIGN ISSUE
AC2 PCB INDOOR BLOWER AND MOTOR FAULTY(2 T GENERAL) | A/C PCB kit is faulty | AIR_CONDITIONER | PCB KIT
LOGOTIMER FAULTY | A/C LOGOTIMER FAULTY | AIR_CONDITIONER | LOGO TIMER
FIBER NOT PROTECTED FROM ODF TO TN | Fiber cable are not secured. | CABLE DRESSING | Fiber
BC WORKING ON AC SUPPLY |  | DESIGN ISSUE | Design Issue
SHELTER ID EMERGENCY LIGHT FAULTY |  | Emergency Light | Emergency Light
1 BB IS WEAK(DENGTA 92AH) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
EXTERNAL ALARMS NOT PATCHED |  | DESIGN ISSUE | Design Issue
EXTERNAL ALARMS NOT PATCHED |  | DESIGN ISSUE | Design Issue
NO LADDER TO ACCESS ANTENNA (RT SITE) |  | DESIGN ISSUE | Design Issue
WEAK BB(SHOTO 190AH) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
CPRI FROM RRU TO BTS NOT ROUTED PROPERLY | CPRI Cable | CABLE DRESSING | CABLE DRESSING
UNDER RATED BB(SHOTO 100AH-4CELLS) | One BB string is Zero/disconnected | BATTERY BACKUP | BATTERY BACKUP
TOWER GROUNDING CABLE STOLEN-LIGHTNING PROTECTOR & BETWEEN BUS BAR |  | GROUNDING | GROUNDING
TOWER GROUNDING CABLE STOLEN-LIGHTNING PROTECTOR |  | GROUNDING | GROUNDING
HOUSEKEEPING REQUIRED(TREE INSIDE BOUNDRY WALL) | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
EXTERNAL ALARMS NOT PATCHED |  | DESIGN ISSUE | Design Issue
SHELTER ID EMERGENCY LIGHT FAULTY |  | Emergency Light | Emergency Light
AC2 CONDENSSOR AND COMPRESSOR CHOCKED | A/C compressor is faulty | AIR_CONDITIONER | Compressor
ACDB LOCK BROKEN |  | OTHERS | OTHERS
Towe Angle Not Fixed Properly |  | CIVIL_WORK | Tower
Tower Supporting rod broken near 1.2 MW Dish |  | CIVIL_WORK | Tower
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
LOGOTIMER FAULTY | A/C LOGOTIMER FAULTY | AIR_CONDITIONER | LOGO TIMER
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Outdoor Delta AC is faulty (EX-E02 C)( HUAWEI DELTA ) |  | DELTA CABINET | DELTA _AIRCON FAULTY
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
NO ACCESS LADDER FOR ANTENNA (5M) |  | DESIGN ISSUE | Design Issue
Outdoor Delta AC is faulty (EX-E02 C)( HUAWEI DELTA ) |  | DELTA CABINET | DELTA _AIRCON FAULTY
LOGO TIMER NOT OK | A/C LOGOTIMER FAULTY | AIR_CONDITIONER | LOGO TIMER
DELTA FILTER NOT OK DAMAGED |  | DELTA CABINET | DELTA_FILTER
Meter Box Fault |  | CIVIL_WORK | ACDB
Weak Battery Backup | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra material (BELONGS TO OMANTEL) |  | EXTRA MATERIAL | EXTRA MATERIAL
BATTERIES MISSING-4 CELLS |  | BATTERY BACKUP | BATTERY BACKUP
CP METER BOX DOOR BROKEN | Power meter Box door hings/fixation required | CIVIL_WORK | ACDB
NO PROPER PLACE TO STAND AND WORK FOR CABINET |  | DESIGN ISSUE | Design Issue
LEAKAGE OBSERVED IN ODU AC2 | LEAKAGE OBSERVED IN ODU AC | AIR_CONDITIONER | LEAKAGE
TOWER LEG BASE BROKEN |  | CIVIL_WORK | CIVIL_WORK
VSAT DISH BASE NOT AS PER STANDARD |  | DESIGN ISSUE | DESIGN ISSUE
WEAK BACKUP(SHOTO 180AH) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
EXTERNAL ALARMS NOT PATCHED |  | DESIGN ISSUE | Design Issue
BATTERIES STOLEN | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BANK | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BANK | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
PAINT WORK REQ IN SHELTER ROOM |  | CIVIL_WORK | Paint Job
HUAWEI OD CABINET AC FAULTY | HUW cabinet Door CLU Faulty | AIR_CONDITIONER | OD CABINET AIR CON
DELTA HANDEL AND LOCK IS FAULTY |  | DELTA CABINET | Door LOCK
DELTA FILTER NOT OK |  | DELTA CABINET | DELTA_FILTER
WALL PAINT/GATE STATUS NOT OK |  | CIVIL_WORK | Paint Job
HUAWEI OD CABINET AC FAULTY | HUW cabinet Door CLU Faulty | AIR_CONDITIONER | OD CABINET AIR CON
VSAT DISH BASE NOT AS PER STANDARD |  | DESIGN ISSUE | DESIGN ISSUE
SITE ID LABEL MISSING |  | LABELING | LABELING
delta cabinet DC aircon compressor is faulty(52270369) |  | OTHERS | Air conditioner
outdoor cabinet door is damaged. |  | CIVIL_WORK | OTHERS
Omantel CP meter box cover broken. | Power meter Box door hings/fixation required (OmanTel) | CIVIL_WORK | ACDB
ACDB opening is blocked 6th energy device. |  | DESIGN ISSUE | DESIGN ISSUE
FOC not properly routed at TN and ODF | FOC cable not arranged properly | CABLE DRESSING | CABLE DRESSING
one angle is broken in site main gate |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
TOWER PAINT REQUIRED |  | CIVIL_WORK | Tower
aviation light is missing Since installation | Aviation light system need to be installed | AVIATION_LIGHT | TOWER
omantel site compound housekeeping required |  | HOUSEKEEPING | HOUSEKEEPING/Omantel
housekeeping required from omantel side |  | HOUSEKEEPING | HOUSEKEEPING/Omantel
tower lightening arrestor grounding cable missing |  | GROUNDING | GROUNDING
tower paint is required |  | CIVIL_WORK | Tower
Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
omantel tower leg foundation is cracked |  | CIVIL_WORK | Tower
RT ladder is rusted and supported by very weak angles |  | CIVIL_WORK | RT Ladder
no dedicated ladder for rooftop antennas |  | DESIGN ISSUE | Design Issue
Dead backup multiple faulty cells found. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Dead backup multiple faulty cells found. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
RT Shelter room has no permanent service wall ladder and the aircons outdoor units are installed on the roof |  | DESIGN ISSUE | DESIGN ISSUE
Tower Lightining Protector grounding has been broken |  | GROUNDING | GROUNDING
Dead backup multiple faulty cells found. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Tower Grounding has been broken. |  | GROUNDING | GROUNDING
Aviation Light main control board has been Faulty / burnt out | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
Tower and Lightining Protector Grounding has been Stolen |  | GROUNDING | GROUNDING
Tower and Lightining Protector Grounding has been Stolen |  | GROUNDING | GROUNDING
Tower and Lightining Protector Grounding has been Stolen |  | GROUNDING | GROUNDING
Tower Grounding has been Broken. |  | GROUNDING | GROUNDING
Tower grounding cable has been broken |  | GROUNDING | GROUNDING
Weak backup multiple faulty cells found. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
TN2P/ODF FIBER DRESSING & RUTTING NOT OK | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Weak / Dead backup multiple faulty cells found. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
One of the MW Dish front cover is missing |  | OTHERS | OTHER
Tower grounding bar has been broken and hanging. |  | GROUNDING | GROUNDING
Tower grounding bar has been broken and hanging. |  | GROUNDING | GROUNDING
Tower Light is not working / Board faulty | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
Rectifier Alarms are not reporting at BBU, seems card faulty. |  | RECTIFIER | Rectifier
LEAKAGE OBSERVED IN ODU AC1 | LEAKAGE OBSERVED IN ODU AC | AIR_CONDITIONER | LEAKAGE
Tower, lighting protector grounding is missing |  | GROUNDING | GROUNDING
Tower, lighting protector grounding is missing |  | GROUNDING | GROUNDING
Main Power CPDB door hings has been broken, therefore door cant close | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
COMPOUND EXCAVATED AS NEW FIBER BEEN LAID |  | CIVIL_WORK | Compound Damage
1 CELL IS FAULTY IN BB1(SHOTO 12V 190AH) |  | BATTERY BACKUP | BATTERY BACKUP
WALL BROKEN |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Sand inside compound |  | CIVIL_WORK | Compound Damage
Main power cable for BTS after swapped activity not under ground |  | CIVIL_WORK | CIVIL_WORK
site gravel required after removal of sand |  | CIVIL_WORK | Compound Damage
site fence is broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site gravel required after removal of sand |  | CIVIL_WORK | Sand
Main gate damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site gravel required |  | CIVIL_WORK | Compound Damage
cable ladder rusted/broken |  | CIVIL_WORK | Cable Tray
tower ladder steps are rusted |  | CIVIL_WORK | Tower
tower foundation base is cracked |  | CIVIL_WORK | Tower
IF cable is lying on the ground | IF cables not arranged properly | CABLE DRESSING | IF
extra material inside compound(dismantiled shelter) |  | EXTRA MATERIAL | EXTRA MATERIAL
4 batteries are faulty(12V/190Ah) |  | BATTERY BACKUP | BATTERY BACKUP
RT dedicated ladder is missing |  | DESIGN ISSUE | Design Issue
LEAKAGE OBSERVED IN AC1 ODU | LEAKAGE OBSERVED IN ODU AC | AIR_CONDITIONER | LEAKAGE
one battery is faulty |  | BATTERY BACKUP | BATTERY BACKUP
no dedicated ladder for rooftop antennas |  | DESIGN ISSUE | Design Issue
3 batteries are faulty |  | BATTERY BACKUP | BATTERY BACKUP
one sector view is blocked by building |  | DESIGN ISSUE | Design Issue
APM30 batteries are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
no dedicated ladder for rooftop antennas |  | DESIGN ISSUE | Design Issue
tower lightining arrestor rod is missing/broken |  | GROUNDING | GROUNDING
Two Tower leg groundings are not available. |  | GROUNDING | GROUNDING
CP meter DB foundation base and door hings has been damaged, need to fix ASAP. | Power meter Box bases completely rusty-Damaged | CIVIL_WORK | ACDB
Hybrid system has been disconnected Completely |  | EXTRA MATERIAL | EXTRA MATERIAL
Site gravel floor has been damaged |  | CIVIL_WORK | Compound Damage
Tower Grounding Stollen |  | GROUNDING | GROUNDING
extra rental DG and fuel tank at site |  | DG ISSUES | DG ISSUES
LEAKAGE OBSERVED IN AC1 | LEAKAGE OBSERVED IN ODU AC | AIR_CONDITIONER | LEAKAGE
Rooftop access ladder is rusted |  | CIVIL_WORK | RT Ladder
site DG is under rated |  | Design Issue | Design Issue
Fire panel not working |  | FIRE EQUIPMENT | FIRE PANEL
Fence safty mesh/angles rusted and broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shelter roof has visual damage,cable ladder need paint job |  | CIVIL_WORK | Paint Job
Tower grounding missing |  | GROUNDING | GROUNDING
aviation light not available | Aviation light system need to be installed | AVIATION_LIGHT | AVIATION_LIGHT
OD Delta shelter Battery bank weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Antenna POLE and Nut Bolts Rusty |  | CIVIL_WORK | Antenna Pole
Tower paint job required /Nut bolts rusted |  | CIVIL_WORK | Paint Job
site gravel required |  | CIVIL_WORK | Compound Damage
site gravel required |  | CIVIL_WORK | Compound Damage
aviation light not available Since Installation | Aviation light system need to be installed | AVIATION_LIGHT | AVIATION_LIGHT
aviation light not isntalled by PT after site relocation | Aviation light system need to be installed | AVIATION_LIGHT | AVIATION_LIGHT
Gravel not done/Fence not installed completely by project team |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Quad switch is not connected to DC power |  | Design Issue | Design Issue
site gravel required |  | CIVIL_WORK | Compound Damage
Manin gate repairning and maintinance required |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
aviation light not installed by project after site relocation | Aviation light system need to be installed | AVIATION_LIGHT | AVIATION_LIGHT
Outdoor Delta AC is faulty (EX-E02 C)( HUAWEI DELTA ) |  | DELTA CABINET | DELTA _AIRCON FAULTY
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup weak & Two bank missing | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery backup weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Tower Lighting rod grounding cable is cut |  | GROUNDING | GROUNDING
Main gate rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
BATTERIES STOLEN | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
DELTA OUTDOOR CABINET AIRCON FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
DELTA DOOR LOCK/HANDLE NOK |  | DELTA CABINET | Door LOCK
DELTA OUTDOOR CABINET AIRCON FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
BATTERIES STOLEN | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
TOWER ROD GROUNDING CABLE STOLEN-LIGHTNING PROTECTOR-30M |  | GROUNDING | GROUNDING
1 AC SPD FAULTY | 1 AC SPD FAULTY | BREAKER/RELAY/SENSOR | AC SPD FAULTY
AC1 COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | A/C COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | AIR_CONDITIONER | Compressor
HUAWEI OUTDOOR CABINET AIRCON FAULTY | HUW cabinet Door CLU Faulty | AIR_CONDITIONER | OD CABINET AIR CON
WEAK BATTERY BACKUP-6 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
1 AC SPD FAULTY | 1 AC SPD FAULTY | BREAKER/RELAY/SENSOR | AC SPD FAULTY
TOWER ROD GROUNDING CABLE STOLEN-LIGHTNING PROTECTOR-20M |  | GROUNDING | GROUNDING
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
HUAWEI OUTDOOR CABINET AIRCON FAULTY | HUW cabinet Door CLU Faulty | AIR_CONDITIONER | OD CABINET AIR CON
DELTA FILTER STATUS NOK(BOTH CAB) |  | DELTA CABINET | DELTA_FILTER
DELTA OUTDOOR CABINET AIRCON FAULTY(SYS) |  | DELTA CABINET | DELTA _AIRCON FAULTY
WEAK BATTERY BACKUP | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
AC1 COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | A/C COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | AIR_CONDITIONER | Compressor
HUAWEI OUTDOOR CABINET AIRCON FAULTY | HUW cabinet Door CLU Faulty | AIR_CONDITIONER | OD CABINET AIR CON
BATTERIES STOLEN | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
WEAK BATTERY BACKUP | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DELTA OUTDOOR CABINET AIRCON FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
LAN SWITCH WORKING ON AC SUPPPLY |  | Wrong Installation | Wrong Installation
SHELTER ID EMERGENCY LIGHT FAULTY |  | Emergency Light | Emergency Light
AC2 COMPLETE UNIT FAUTY(DAIKIN) | A/C compressor is faulty | AIR_CONDITIONER | Compressor
HUAWEI OD CABINET AC FAULTY | HUW cabinet Door CLU Faulty | AIR_CONDITIONER | OD CABINET AIR CON
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
DELTA OUTDOOR CABINET AIRCON FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
AC2 COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | A/C COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | AIR_CONDITIONER | Compressor
AIRCON CONTROL DB FAULTY | A/C CONTROL Panel is FAULTY | AIR_CONDITIONER | Control Panel
2 CELLS MISSING FROM BATTERY BANK |  | BATTERY BACKUP | BATTERY BACKUP
TOWER ROD STATUS NOT OK |  | GROUNDING | GROUNDING
DELTA OUTDOOR CABINET AIRCON FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
FENCE/GATE MISSING |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
DELTA DOOR LOCK/HANDLE NOK |  | DELTA CABINET | Door LOCK
SIGGOS PROBE WORKING ON AC SUPPPLY |  | Wrong Installation | Wrong Installation
EQUIPMENT WORKING ON AC SUPPPLY IN BOTH SHELTER |  | Wrong Installation | Wrong Installation
shelter paint required |  | CIVIL_WORK | Indoor Shelter
tower paint required |  | CIVIL_WORK | Tower
shelter roof is completely damged(leakges from top) |  | CIVIL_WORK | Indoor Shelter
shelter paint required |  | CIVIL_WORK | Indoor Shelter
site main gate angles are rusted and broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
tower paint required |  | CIVIL_WORK | Tower
DG ATS glass cover is broken |  | DG ISSUES | DG ISSUES
all COW guy wires are loose one wire is completely removed |  | CIVIL_WORK | Tower
one COW leg is not vertical |  | CIVIL_WORK | Tower
Batteries are Damage |  | BATTERY BACKUP | BATTERY BACKUP
Site fence is broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
COW spare tyre not availble |  | OTHERS | COW tyre
COW cage need to paint |  | COW | COW
EXTRA MATERIAL(ODF-RACK) |  | EXTRA MATERIAL | EXTRA MATERIAL
General Air-Con #02 has been faulty (PCB KIT) hence 1st aircon is working on manual mode. | A/C PCB kit is faulty | AIR_CONDITIONER | PCB Kit
EXTRA MATERIAL(AGISSON RECTIFIER) |  | EXTRA MATERIAL | EXTRA MATERIAL
TOWER ROD GROUNDING CABLE STOLEN-30M |  | GROUNDING | GROUNDING
DELTA FILTER STATUS NOK(BOTH CAB) |  | DELTA CABINET | DELTA_FILTER
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
AIRCON CONTROL DB FAULTY(TN SHELTER) | A/C CONTROL Panel is FAULTY | AIR_CONDITIONER | Control Panel
AC1 COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | A/C COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | AIR_CONDITIONER | Compressor
NO ALARMS PATCHED ON TN |  | Design Issue | Design Issue
DG BODY RUSTY |  | DG ISSUES | DG ISSUES
WRONG INSTALLATION OF RRU DUE TO WHICH AC CONTROL DB UNABLE TO OPEN FOR MAINTIANENCE |  | DESIGN ISSUE | DESIGN ISSUE
WEAK BATTERY BACKUP(1 BANK) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
SHELTER ID EMERGENCY LIGHT FAULTY |  | Emergency Light | Emergency Light
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
DELTA OUTDOOR CABINET AIRCON FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
DELTA OUTDOOR CABINET AIRCON FAULTY(BOTH CAB) |  | DELTA CABINET | DELTA _AIRCON FAULTY
DELTA OUTDOOR CABINET AIRCON FAULTY(BOTH CAB) |  | DELTA CABINET | DELTA _AIRCON FAULTY
DELTA FILTER STATUS NOK(BOTH CAB) |  | DELTA CABINET | DELTA_FILTER
EXTRA MATERIAL(RACK CONTAINING SHOTO BATTERIES) |  | EXTRA MATERIAL | EXTRA MATERIAL
SEEPAGE FOUNDED IN WALL |  | CIVIL_WORK | Indoor Shelter
AC2 COMPRESSOR FAULTY(PISTON,2.5T,TOSHIBA) | AC COMPRESSOR FAULTY(PISTON,2.5T,TOSHIBA) | AIR_CONDITIONER | Compressor
EXTRA MATERIAL(ANTENNA BELONGS TO OT) |  | EXTRA MATERIAL | EXTRA MATERIAL
DELTA OUTDOOR CABINET AIRCON FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
EXTRA MATERIAL(OSN RACK PDU) |  | EXTRA MATERIAL | EXTRA MATERIAL
AC2 COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | A/C COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | AIR_CONDITIONER | Compressor
EXTRA MATERIAL(ERCISSON RECTIFIER) |  | EXTRA MATERIAL | EXTRA MATERIAL
GATE RUSTY |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
EXTRA MATERIAL(FUEL TANK TRAY) |  | EXTRA MATERIAL | EXTRA MATERIAL
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
DELTA DOOR LOCK/HANDLE NOK |  | DELTA CABINET | Door LOCK
General Air-Con #02 has been faulty (gas leackege) hence 1st aircon is working on manual mode. | LEAKAGE OBSERVED IN ODU AC | AIR_CONDITIONER | LEAKAGE
Cable Ladder Base rusted/ broken |  | CIVIL_WORK | Cable Tray
Tower supporting rods are broken |  | CIVIL_WORK | Tower
Shoto 190Ah 8 Battery cell faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
seepage & crack inside room |  | CIVIL_WORK | Indoor Shelter
EXTRA MATERIALS AT SITE |  | EXTRA MATERIAL | EXTRA MATERIAL
Battery backup weak rectifire one | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
RECTIFIER DPS2900B SUPERVISION MODULE (PSC 3) FAULTY |  | RECTIFIER | RECTIFIER MODULE
NO ACCESS LADDER FOR ANTENNA & OUTDOOR AC(5M) |  | DESIGN ISSUE | DESIGN ISSUE
RECTIFIER DPS2900B SUPERVISION MODULE (PSC 3) FAULTY |  | RECTIFIER | RECTIFIER MODULE
trees inside omantel compound |  | HOUSEKEEPING | HOUSEKEEPING/Omantel
equipment room door hinges are broken |  | CIVIL_WORK | Indoor Shelter
tower foundation is cracked |  | CIVIL_WORK | Tower
Site main gate is completely broken/detached from pillers |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
AC power cable duct is rusted. |  | CIVIL_WORK | OTHERS
5G installation not properly done with wrong cable arrangments |  | Wrong Installation | Wrong Installation
one battery is faulty |  | BATTERY BACKUP | BATTERY BACKUP
battery backup is zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
DG alarm not working due to faulty relay in DG |  | DG ISSUES | DG ISSUES
ERICSSON PBC OUTDOOR CABINET DC AIRCON IS FAULTY. | Ericsson Outdoor Cabinet AC Faulty | AIR_CONDITIONER | OD CABINET AIR CON
site main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
tower lightening arrestor rod is missing |  | Grounding | Grounding
CP meter screen is damged |  | OTHERS | others
two batteries are faulty |  | BATTERY BACKUP | BATTERY BACKUP
tower lightening arrestor rod is missing |  | Grounding | Grounding
Huawei outdoor cabinet aircon compressor faulty | HUW cabinet Door CLU Faulty | AIR_CONDITIONER | OD CABINET AIR CON
lightening arrestor rod is damaged |  | Grounding | Grounding
Extra Material At site |  | Extra Material | Extra Material
HOUSEKEEPING REQUIRED(greenry at site compound) | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
DELTA OUTDOOR CABINET AIRCON FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
DELTA DOOR LOCK NOK |  | DELTA CABINET | Door LOCK
1 HUAWEI RECTIFIER MODULE FAULTY( TP48400B N20C1) |  | RECTIFIER | RECTIFIER MODULE
HUAWEI RECTIFIER SMU MISSING(ETP48300C5A1) |  | RECTIFIER | RECTIFIER MODULE
EXTRA MATERIAL(BELONG TO OT) |  | EXTRA MATERIAL | EXTRA MATERIAL
BATTERIES STOLEN(8 CELLS) | Batteries were stolen | BATTERY BACKUP | BATTERY BACKUP
Both Two air con are working on Hand mode | Both aircons are working on manual mode | AIR_CONDITIONER | Hand Mode
Both Two AC\'s are on hand mode as logo-timer is faulty | A/C LOGOTIMER FAULTY | AIR_CONDITIONER | LOGO TIMER
WEAK BATTERY BACKUP(SHOTO 12V 190AH, 8CELLS) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Both two A/Cs are working on Hand mode | Both aircons are working on manual mode | AIR_CONDITIONER | Hand Mode
DELTA OUTDOOR CABINET AIRCON FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
WEAK BATTERY BACKUP(BOTH RECT) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Both two A/Cs are working on Hand mode | Both aircons are working on manual mode | AIR_CONDITIONER | Hand Mode
UEIU CARD NOT (HT ALARM NOT REPORTED) |  | OTHERS | OTHERS
WEAK BATTERY BACKUP(DENGTA 12V 150AH, 16CELLS) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DELTA DOOR LOCK/HANDLE NOK |  | DELTA CABINET | Door LOCK
DELTA RECTIFIER CONTROLLER FAULTY(PSC3) |  | DELTA CABINET | RECTIFIER MODULE
Both 2 A/C\'s OD units are covered by Hill fallen down rocks and dust so both are on OFF mode | OD units physical condition bad/Damages | AIR_CONDITIONER | AIR CONTIONER ODU
AC1 FAULTY | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Sand Dunes are inside the site |  | CIVIL_WORK | Sand
Both 2 A/C\\\'s are working on H mode | Both aircons are working on manual mode | AIR_CONDITIONER | Hand Mode
AIRCON LOGOTIMER FAULTY(NA IN W/H) | A/C LOGOTIMER FAULTY | AIR_CONDITIONER | LOGO TIMER
ERICSSON PBC OUTDOOR CABINET DOOR IS NOT LOCKED BECAUSE OF TEMP AS DC AIRCON IS FAULTY. |  | OTHERS | others
Extra MATERIAL INDOOR SHELTER AVAILABLE AT SITE WITH GENERAL 18000BTU AIRCONS AND SMDB ETC.. |  | EXTRA MATERIAL | EXTRA MATERIAL
AIRCON LOGOTIMER FAULTY(NA IN W/H) | A/C LOGOTIMER FAULTY | AIR_CONDITIONER | LOGO TIMER
AIRCON LOGOTIMER FAULTY(MISSING IN W/H) | A/C LOGOTIMER FAULTY | AIR_CONDITIONER | LOGO TIMER
MF200 FACP battery has been faulty and not available at warehouse yet. |  | FIRE EQUIPMENT | Fire Equipment
Tower and Lightining Protector Grounding has been Stolen |  | GROUNDING | GROUNDING
WEAK backup multiple weak cells found. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Tower and Lightining Protector Grounding has been Stolen |  | GROUNDING | GROUNDING
Tower Lightining Protector grounding has been broken |  | GROUNDING | GROUNDING
OD MW IF cable needs to be arrange properly, hanging inside the tower | IF cables not arranged properly | CABLE DRESSING | IF
Antennas jumper cables and MW IF cables need to route properly, cable ties required. |  | OTHERS | OTHER
MW IF cables need to arrange and fix properly, cable ties required. |  | OTHERS | OTHER
AIRCON LOGOTIMER FAULTY(MISSING IN W/H) | A/C LOGOTIMER FAULTY | AIR_CONDITIONER | LOGO TIMER
Site Access Ladder is totally Rusted |  | CIVIL_WORK | RT Ladder
Fence totally rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Wall Paint totally damage need wall repairing |  | CIVIL_WORK | Paint Job
Extra materials inside site boundary |  | EXTRA MATERIAL | EXTRA MATERIAL
Extra materials inside site boundary |  | EXTRA MATERIAL | EXTRA MATERIAL
Extra materials inside site boundary |  | EXTRA MATERIAL | EXTRA MATERIAL
Extra materials inside site boundary |  | EXTRA MATERIAL | EXTRA MATERIAL
4 batteries are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
RT access ladder is missing |  | CIVIL_WORK | RT Ladder
cable ladder is rusted outside shelter |  | CIVIL_WORK | Cable Tray
no dedicated ladder for rooftop |  | CIVIL_WORK | RT Ladder
Battery backup is zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
shelter door is damaged cannot be CLOSED properly need to replace |  | CIVIL_WORK | Indoor Shelter
tower paint required |  | civIL_WORK | Tower
tower foundation is cracked. |  | CIVIL_WORK | Tower
site fence is damaged from one side. |  | cIVIL_WORK | Fence / Boundry Wall / Main Gate
shelter paint required |  | CIVIL_WORK | Indoor Shelter
site main gate paint required |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
tower grounding strip is detached |  | GROUNDING | GROUNDING
1 battery is faulty |  | BATTERY BACKUP | BATTERY BACKUP
ACDB is completely damaged |  | CIVIL_WORK | ACDB
fence is damaged at some points need rectification. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
all batteries in APM30 and 4 batteries in OG rack are faulty |  | BATTERY BACKUP | BATTERY BACKUP
all batteries are dead | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Wimax antenna clamps are rusted |  | CIVIL_WORK | Antenna Pole
ACDB cover lock is broken | Power meter Box door hings/fixation required | CIVIL_WORK | ACDB
aviation light is broken on omantel tower | Aviation light system is not working, Need Replace | AVIATION_LIGHT | AVIATION_LIGHT
omantel site main gate not properly closing |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
extra material inside shelter.(LTE-TDD) |  | Extra material | Extra material
shelter paint required |  | CIVIL_WORK | Indoor Shelter
site main gate paint required |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site fence is rusted need to repaint |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Tower second stay is rusted. |  | CIVIL_WORK | Cable Tray
shelter roof is rusted |  | CIVIL_WORK | Indoor Shelter
extra material inside shelter. |  | Extra material | Extra material
OSN shelter roof is rusted. |  | CIVIL_WORK | Indoor Shelter
boundry wall is damaged. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site main gate paint required |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
tower groundig strip is broken |  | Grounding | Grounding
all batteries are faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
site fence need to repaint |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
extra material inside compound.VSAT Antenna,SIU and Convertor |  | Extra material | Extra material
tower ladder is rusted |  | CIVIL_WORK | Tower
cable ladder is rusted. |  | CIVIL_WORK | Cable Tray
all batteries are faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
RT access ladder is badly rused need to replace |  | CIVIL_WORK | RT Ladder
Extra material is at site. |  | Extra material | Extra material
TOWER GROUNDING STOLEN-LIGHTNING PROTECTOR-45M |  | GROUNDING | GROUNDING
TOWER PAINT REQUIRED |  | CIVIL_WORK | Paint Job
FENCE E IS RUSTED |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
TOWER PAINT REQUIRED |  | CIVIL_WORK | Paint Job
TOWER GROUNDING LIGHTNING PROTECTOR IS BROKEN |  | GROUNDING | GROUNDING
TOWER GROUNDING LIGHTNING PROTECTOR IS BROKEN |  | GROUNDING | GROUNDING
SITE MAIN DOOR DAMAGED |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site main gate padlock is missing | Site main gate padlock is missing (Omantel as Host) | PADLOCK | PADLOCK/Omantel
Sand inside compound |  | CIVIL_WORK | Sand
Tower aviation light Fully System Rusted & Faulty | Aviation light system is not working, Need Replace | AVIATION_LIGHT | AVIATION_LIGHT
Sand inside compound |  | CIVIL_WORK | Sand
Sand inside compound |  | CIVIL_WORK | Sand
Sand inside compound |  | CIVIL_WORK | Sand
TOWER GROUNDING STOLEN-LIGHTNING PROTECTOR-65M |  | GROUNDING | GROUNDING
DG Fuel Tank Foundatin Need to Fix |  | CIVIL_WORK | Foundation
EXTRA MATERIALS AT SITE (MW DISH) |  | Extra material | Extra material
Housekeeping required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
SMU OF RECTIFIER 2 IN SDH SHELTER FAULTY |  | RECTIFIER | RECTIFIER
AVR is faulty |  | OTHERS | AVR
Housekeeping required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Site fence mesh is damaged from one side |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site main gate paint required |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Battery Backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery String2 breaker is faulty |  | RECTIFIER | RECTIFIER
Battery Backup for OG rack and APM30H is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra material inside shelter(empty OSN RACK) |  | Extra material | Extra material
Monopole tower safety rail is damaged |  | CIVIL_WORK | Tower
Site fence mesh is damaged from one side |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Battery Backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
no dedicated ladder for rooftop antennas |  | CIVIL_WORK | RT Ladder
Battery fuse breaker is faulty for string 1 |  | RECTIFIER | RECTIFIER
RT antenna mount poles are rusted |  | CIVIL_WORK | Antenna Pole
Shoto 12V/190A(8 bateery) weak battery Backup | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Full Fence is not lavel and wire loose |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Fence fallen Down |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main Gate not closed properly Fence fallen Down |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
extra material at site( VSET indoor and outdoor) |  | EXTRA MATERIAL | EXTRA MATERIAL
Site main gate padlock is missing(Omantel as Host) | Site main gate padlock is missing (Omantel as Host) | PADLOCK | PADLOCK/Omantel
Site main gate padlock is missing(Omantel as Host) | Site main gate padlock is missing (Omantel as Host) | PADLOCK | PADLOCK/Omantel
Shoto 12V/190A(8 bateery) weak battery Backup | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site main gate padlock is missing(Omantel as Host) | Site main gate padlock is missing (Omantel as Host) | PADLOCK | PADLOCK/Omantel
Hybrid DG Door locks faulty |  | DG ISSUES | DG ISSUES
Shelter need paint job |  | CIVIL_WORK | Paint Job
Sand inside compound |  | CIVIL_WORK | Sand
Housekeeping required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
DELTA OUTDOOR CABINET AIRCON FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
DELTA RECTIFIER MODULE FAULTY |  | DELTA CABINET | RECTIFIER MODULE
EXTRA MATERIAL (3 ANTENNA PIPES & BRACKETS OUTSIDE SHELTER) |  | EXTRA MATERIAL | EXTRA MATERIAL
DELTA DOOR LOCK/HANDLE NOK |  | DELTA CABINET | Door LOCK
DELTA DOOR LOCK/HANDLE NOK |  | DELTA CABINET | Door LOCK
AC1 COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | A/C COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | AIR_CONDITIONER | Compressor
EXTRA MATERIAL (3 ANTENNA PIPES OUTSIDE SHELTER) |  | EXTRA MATERIAL | EXTRA MATERIAL
DELTA OUTDOOR CABINET AIRCON FAULTY |  | Delta Cabinet | DELTA _AIRCON FAULTY
Major Housekeeping Required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
DELTA RECTIFIER MODULE FAULTY |  | DELTA CABINET | RECTIFIER MODULE
DELTA OUTDOOR CABINET AIRCON FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
DELTA DOOR LOCK/HANDLE NOK |  | DELTA CABINET | Door LOCK
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
EXTRA MATERIAL (DISMANTLED PBC6500) |  | EXTRA MATERIAL | EXTRA MATERIAL
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP-16 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
EXTRA MATERIAL (DISMANTLED ERCISSON TN MINI CABINET) |  | EXTRA MATERIAL | EXTRA MATERIAL
AC1 GENERAL AOG30AMAH ROTARY OUTDOOR COMPRESSOR FAULT | A/C COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | AIR_CONDITIONER | Compressor
two rectifier modules are not working |  | RECTIFIER | RECTIFIER
Housekeeping required( Labor Required) | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
DELTA DOOR LOCK/HANDLE NOK |  | DELTA CABINET | Door LOCK
GROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR-35M) |  | GROUNDING | GROUNDING
GROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR-30M) |  | GROUNDING | GROUNDING
Housekeeping required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
MAIN GROUNDING BUS BAR MISSING |  | GROUNDING | GROUNDING
LEAKAGE OBSERVED IN AC1(R410 GAS) | LEAKAGE OBSERVED IN AC (R410 GAS) | AIR_CONDITIONER | Compressor
DELTA RECTIFIER MODULE FAULTY |  | DELTA CABINET | RECTIFIER MODULE
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
EXTRA MATERIAL (VSAT DISH & MODEM) |  | EXTRA MATERIAL | EXTRA MATERIAL
GROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR-30M) |  | GROUNDING | GROUNDING
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
WEAK BATTERY BACKUP IN OD CABINET-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
AC2 FAULTY (LG) | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
AIRCON LOGOTIMER FAULTY(MISSING IN W/H) | A/C LOGOTIMER FAULTY | AIR_CONDITIONER | LOGO TIMER
EXTRA MATERIAL (DISMANTLED RECTIFIER AND METRO SWITCH) |  | EXTRA MATERIAL | EXTRA MATERIAL
EXTRA MATERIAL (DISMANTLED RECTIFIER, METRO SWITCH AND UPM) |  | EXTRA MATERIAL | EXTRA MATERIAL
DELTA RECTIFIER MODULE FAULTY(3) |  | DELTA CABINET | RECTIFIER MODULE
EXTRA MATERIAL (DISMANTLED METRO SWITCH) |  | EXTRA MATERIAL | EXTRA MATERIAL
EXTRA MATERIAL (DISMANTLED APM30H) |  | EXTRA MATERIAL | EXTRA MATERIAL
AC1 PISTON 2.5T COMPRESSOR FAULTY (GENERAL) | AC COMPRESSOR FAULTY(PISTON,21.5T,General) | AIR_CONDITIONER | Compressor
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
DELTA FILTER STATUS NOK(2) |  | DELTA CABINET | DELTA_FILTER
GROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR-35M) |  | GROUNDING | GROUNDING
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
GROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR-35M) |  | GROUNDING | GROUNDING
AC2 ROTARY 2.5T COMPRESSOR FAULTY (GENERAL) | AC COMPRESSOR FAULTY(PISTON,21.5T,General) | AIR_CONDITIONER | Compressor
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
AIRCON LOGOTIMER FAULTY(MISSING IN W/H) | A/C LOGOTIMER FAULTY | AIR_CONDITIONER | LOGO TIMER
SDG is not Working |  | DG ISSUES | DG ISSUES
Extra Material at site ( RF Antenna/Antenna Mount) |  | EXTRA MATERIAL | EXTRA MATERIAL
Extra L-Rack Inside Shelter |  | EXTRA MATERIAL | EXTRA MATERIAL
Extra Shelter with Ericsson equiipment and civil mount and poles |  | EXTRA MATERIAL | EXTRA MATERIAL
no fence or boundary wall |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site main gate padlock is missing(Omantel as Host) | Site main gate padlock is missing | PADLOCK | PADLOCK
extra material at site( U clumps and mount Breaket Omantel Metrial) |  | EXTRA MATERIAL | EXTRA MATERIAL
Shelter need paint job |  | CIVIL_WORK | Shelter
Shoto 12V/190A(8 bateery) weak battery Backup | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Shoto 12V/100A(8 bateery for TDD) weak battery Backup | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Shoto 12V/190A(8 bateery) weak battery Backup | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Shoto 12V/190A(8 bateery) weak battery Backup | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Shoto 12V/190A(8 bateery) weak battery Backup | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Shoto 12V/190A(8 bateery) weak battery Backup | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Shoto 12V/190A(8 bateery) weak battery Backup | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Shoto 12V/190A(8 bateery) weak battery Backup | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Shoto 12V/190A(8 bateery) weak battery Backup | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Shoto 12V/190A(8 bateery) weak battery Backup | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Shoto 190Ah 8 Battery cell faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Shoto 190Ah 8 Battery cell faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Shoto 190Ah 8 Battery cell faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Shoto 190Ah 8 Battery cell faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
ASCOT SDG Faulty |  | DG ISSUES | DG ISSUES
ASCOT SDG Faulty |  | DG ISSUES | DG ISSUES
aircon condensor is damaged. | A/C compressor is Damaged | AIR_CONDITIONER | Condensor
EXTRA MATERIAL(VSAT DISH, MODEM) |  | EXTRA MATERIAL | EXTRA MATERIAL
WEAK BATTERY BACKUP-8 CELLS GU RECTIFIER | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
AVR FAULTY |  | OTHERS | others
WEAK BATTERY BACKUP-8 CELLS GU RECTIFIER | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
GROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR) |  | GROUNDING | GROUNDING
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
OUTDOOR BULB SET BROKEN |  | OTHERS | others
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP-16CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
housekeeping required-major | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
AC2 ROTARY 2.5T COMPRESSOR FAULTY | A/C COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | AIR_CONDITIONER | Compressor
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
EXTRA MATERIAL(antenna pole outside shelter) |  | EXTRA MATERIAL | EXTRA MATERIAL
WEAK BATTERY BACKUP-4CELLS for TDD rectifier | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Door lock is Faulty |  | CIVIL_WORK | CIVIL_WORK
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
3 Phase Power cable from cp meter to site is faulty(50m) |  | OTHERS | others
AC2 PCB KIT MISSING(2.5T TOSHIBA) | A/C PCB kit is faulty | AIR_CONDITIONER | PCB Kit
EXTRA MATERIAL(emerson rectifier in gul shelter, no load connected) |  | EXTRA MATERIAL | EXTRA MATERIAL
DELTA OUTDOOR CABINET AIRCON FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
WEAK BATTERY BACKUP-12 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DELTA RECTIFIER MODULE FAULTY |  | DELTA CABINET | RECTIFIER MODULE
GROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR-30M) |  | GROUNDING | GROUNDING
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
AC2 ODU have leakage | LEAKAGE OBSERVED IN ODU AC | AIR_CONDITIONER | LEAKAGE
WEAK BATTERY BACKUP-8 CELLS 100ah | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
housekeeping required-major | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
EXTRA MATERIAL(DISMANTLED PBC6500) |  | EXTRA MATERIAL | EXTRA MATERIAL
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
EXTRA MATERIAL(DISMANTLED RECTIFIER IN BOTH SHELTER) |  | EXTRA MATERIAL | EXTRA MATERIAL
AC1 ROTARY 2.5T COMPRESSOR FAULTY | A/C COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | AIR_CONDITIONER | Compressor
AC-2 is on off mode. | One A/C is working on manual mode | AIR_CONDITIONER | Hand Mode
AC2 ROTARY 2.5T COMPRESSOR FAULTY | A/C COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | AIR_CONDITIONER | Compressor
AC2 INDOOR CARD FAULTY TOSHIBA INDOOR:RAS-30UKP-AR3 (2.5) | A/C PCB kit is faulty | AIR_CONDITIONER | PCB KIT
WEAK BATTERY BACKUP-16 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP-16 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP-4 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BB IN GU CAB- 8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
AC-2 is on off mode. | One A/C is working on manual mode | AIR_CONDITIONER | Hand Mode
DELTA OUTDOOR CABINET AIRCON FAULTY(BATTERY CABINET) |  | DELTA CABINET | DELTA _AIRCON FAULTY
DELTA FILTER STATUS NOK(BATTERY CABINET) |  | DELTA CABINET | DELTA_FILTER
GROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR-30M) |  | GROUNDING | GROUNDING
DELTA FILTER STATUS NOK |  | DELTA CABINET | DELTA_FILTER
AC2 ROTARY 2.5T COMPRESSOR FAULTY (GENERAL) | A/C COMPRESSOR FAULTY(ROTARY,2.5T,GENERAL ASG30AMAH) | AIR_CONDITIONER | Compressor
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
EXTRA MATERIAL(2 DISMANTLED METRO3100 AND OSN CABINET ) |  | EXTRA MATERIAL | EXTRA MATERIAL
ROOM PAINT NOT OK(MAJOR) |  | CIVIL_WORK | CIVIL_WORK
WEAK BATTERY BACKUP-8 CELLS OF RECTIFIER 1 | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
EXTRA MATERIAL(L rack outside shelter ) |  | EXTRA MATERIAL | EXTRA MATERIAL
DELTA FILTER |  | DELTA CABINET | DELTA_FILTER
DELTA RECTIFIER CONTROLLER FAULTY(PSC3) |  | DELTA CABINET | DELTA RECTIFIER
DELTA DOOR LOCK/HANDLE NOK |  | DELTA CABINET | DELTA CABINET
WEAK BATTERY BACKUP-4 CELLS 40AH | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DELTA OUTDOOR CABINET AIRCON FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
DELTA DOOR LOCK/HANDLE NOK |  | DELTA CABINET | DELTA CABINET
WEAK BATTERY BACKUP-12 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP-16 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DOOR BROKEN(BELONGS TO OMANAIR MAINT.) |  | CIVIL_WORK | CIVIL_WORK
EXTRA MATERIAL(PBC6500 ) |  | EXTRA MATERIAL | EXTRA MATERIAL
EXTRA MATERIAL(OSN CABINET OUTSIDE SHELTER) |  | EXTRA MATERIAL | EXTRA MATERIAL
TOWERG ROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR-30M) |  | GROUNDING | GROUNDING
TOWERG ROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR-10M) |  | GROUNDING | GROUNDING
TOWERG ROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR-30M) |  | GROUNDING | GROUNDING
TOWERG ROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR-30M) |  | GROUNDING | GROUNDING
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
TOWERG ROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR-30M) |  | GROUNDING | GROUNDING
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP-8 CELLS | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
EXTRA MATERIAL(CALL OUT DG) |  | EXTRA MATERIAL | EXTRA MATERIAL
WRONG INSTALLTION OF SAFETY CAGE,UNABLE TO OPEN DOOR |  | OTHERS | others
AC-2 is on off mode. | One A/C is working on manual mode | AIR_CONDITIONER | Hand Mode
GND CABLE STOLEN 15 M |  | GROUNDING | GROUNDING
TOWER GROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR-30M) |  | GROUNDING | GROUNDING
DOOR BROKEN(EQUIPMENT ROOM) |  | CIVIL_WORK | SHELTER
FENCE NOT OK |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
BATTERIES ARE FAULTY, BACKUP IS LESS THAN 1 MINUTE. | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
EXTRA MATERIAL AT SITE. Project materials left over. |  | EXTRA MATERIAL | EXTRA MATERIAL
BOUNDARIES WALL/FENCE NOT AVAILABLE. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
EXTRA MATERIAL AT SITE: CABLES, MW DISH, UPM POWER SUPPLY. |  | EXTRA MATERIAL | EXTRA MATERIAL
EXTRA MATERIAL AT SITE. OLD SDG WITH FUEL TANK AND ATS PANEL. |  | EXTRA MATERIAL | EXTRA MATERIAL
SITE BACK SIDE FENCE IS DAMAGED, HAS A BIG HOLE IN IT. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
EXTRA MATERIAL AT SITE. UPM POWER SUPPLY IN OSN RACK |  | EXTRA MATERIAL | EXTRA MATERIAL
EXTRA MATERIAL AT SITE, ATN950D PACKING BOXES ETC. |  | EXTRA MATERIAL | EXTRA MATERIAL
EXTRA MATERIAL AVAILABLE., UPM POWER SUPPLY IN OSN RACK. |  | EXTRA MATERIAL | EXTRA MATERIAL
FIBER CABLES NEED TO BE SECURE IN TRANSMISSION RACK. | Fiber cable are not secured. | CABLE DRESSING | Fiber
FIBER CABLES NOT SECURED IN TRANSMISSION RACK. | Fiber cable are not secured. | CABLE DRESSING | Fiber
FIBER CABLES NOT SECURED IN TRANSMISSION RACK. | Fiber cable are not secured. | CABLE DRESSING | Fiber
FIBER CABLES NEED TO BE SECURED IN TRANSMISSION RACK. | Fiber cable are not secured. | CABLE DRESSING | Fiber
EXTRA MATERIAL AT SITE. FIBER CABLE. | Fiber cables not arranged properly | CABLE DRESSING | Fiber
EXTRA MATERIAL AT SITE, VSAT DISH WITH ITS NE. |  | EXTRA MATERIAL | EXTRA MATERIAL
EXTRA MATERIAL AT SITE. VSAT DISH WITH ITS NE |  | EXTRA MATERIAL | EXTRA MATERIAL
OG RECTIFIER_01 BATTERIES ARE FAULTY. |  | BATTERY BACKUP | BATTERY BACKUP
BATTERIES ARE FAULTY. ZERO BACKUP. | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
EXTRA MATERIAL AT SITE, ATN CABINET |  | EXTRA MATERIAL | EXTRA MATERIAL
Site Pathway is damaged |  | CIVIL_WORK | PATHWAY DAMAGE
Tower aviation light Board faulty | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
Extra VSAT Dish with Modem |  | EXTRA MATERIAL | EXTRA MATERIAL
Extra VSAT Dish with Modem |  | EXTRA MATERIAL | EXTRA MATERIAL
EXTRA MATERIAL AT SITE, ETP48300C5A1 POWER SYSTEM |  | EXTRA MATERIAL | EXTRA MATERIAL
GROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR-35M) with grounding cable from shelter busbat to earth pit |  | GROUNDING | Grounding
grounding cable from sector 3 rru and pole to main bus bar missing |  | GROUNDING | grounding
Battery Backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Delta Air con Filter is damage | Delta Cabinet A/C Filter is damage | AIR_CONDITIONER | OD CABINET AIR CON
Delta Air con Filter is damage |  | DELTA CABINET | Filter
DELTA OUTDOOR CABINET AIRCON FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
DELTA FILTER NOT OK |  | DELTA CABINET | DELTA_FILTER
DELTA RECTIFIER MODULE FAULTY(2) |  | DELTA CABINET | DELTA RECTIFIER
EXTRA MATERIAL(DISMANTLED ERICSSON OUTDOOR CABINET) |  | EXTRA MATERIAL | EXTRA MATERIAL
DELTA FILTER NOT OK |  | DELTA CABINET | DELTA_FILTER
EXTRA MATERIAL(DISMANTLED OUTDOOR CABINET-BELONGS TO OT) |  | EXTRA MATERIAL | EXTRA MATERIAL
GROUNDING CABLE STOLEN(TOWER LIGHTNING PROTECTOR-30M) |  | GROUNDING | GROUNDING
housekeeping required-major | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Site Tower Foundation damage due to Rain |  | CIVIL_WORK | Foundation
Site Tower Foundation damage due to Rain |  | CIVIL_WORK | Foundation
EXTRA MATERIAL AT SITE, VSAT DISH WITH ITS NE. |  | Extra Material | Extra Material
EXTRA MATERIAL AT SITE, VSAT DISH WITH ITS NE. |  | Extra Material | Extra Material
outdoor CP db broken | Power meter Box door hings/fixation required | CIVIL_WORK | ACDB
grounding cable from shelter main busbar to earthing pit missing |  | GROUNDING | GROUNDING
tower grounding cable is missing |  | GROUNDING | GROUNDING
Grounding cable from shelter indoor busbar to main bus bar is missing |  | GROUNDING | GROUNDING
Outdoor Delta AC is faulty (EX-E02 C)( HUAWEI DELTA ) |  | DELTA CABINET | DELTA _AIRCON FAULTY
EXTRA MATERIAL AT SITE, RF Antenna inside the shelter |  | Extra Material | Extra Material
EXTRA MATERIAL AT SITE, OMANTEL RF Antennas |  | Extra Material | Extra Material
EXTRA MATERIAL AT SITE UPM POWER SUPPLY IN OSN RACK. |  | Extra Material | Extra Material
EXTRA MATERIAL AT SITE, A Fuel Tank 3000Ltrs |  | Extra Material | Extra Material
EXTRA MATERIAL AT SITE, METRO3100, SOME BOXES IN OSN SHELTER. |  | Extra Material | Extra Material
AVR IS FAULTY, HENCE BYPASSED. |  | OTHERS | AVR
EXTRA MATERIAL AT SITE, Dismanteled Ericsson cabinets are outside. |  | Extra Material | Extra Material
AVR is faulty |  | OTHERS | AVR
House keeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
House keeping is required. | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
DELTA FILTER NOT OK |  | DELTA CABINET | DELTA_FILTER
Extra Material(dismantled cabinet belongs to OT) |  | Extra Material | Extra Material
WEAK BATTERY BACKUP(SHOTO 100AH, 8 CELLS, TDD APM) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra Material(dismantled cabinet belongs to OT) |  | Extra Material | Extra Material
Extra Material(dismantled cabinet belongs to OT) |  | Extra Material | Extra Material
DELTA FILTER NOT OK |  | DELTA CABINET | DELTA_FILTER
DELTA FILTER NOT OK |  | DELTA CABINET | DELTA_FILTER
TOWER GROUNDING STRIP FALLEN TO GROUND |  | GROUNDING | GROUNDING
EXTRA MATERIAL(DISMANTLED MW DISH BY PT) |  | Extra Material | Extra Material
WEAK BATTERY BACKUP(SHOTO 190AH, 8 CELLS) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
concrete earth pit damage |  | CIVIL_WORK | COMPOUND
2G 3G cabinet site ID yellow label missing |  | LABELING | LABELING
AC power DB meter glass missing | Power meter Box glass missing | CIVIL_WORK | ACDB
GU cabinet BB is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
FE is missing |  | FIRE EXTINGUISER | MISSING
BTS room Numerical Lock is faulty |  | CIVIL_WORK | SHELTER
BTS room roof seepage and cracking |  | CIVIL_WORK | SHELTER
Shelter Cleaning is required |  | OTHERS | OTHERS
Rectifier dummy is missing |  | DUMMY MISSING | DUMMY MISSING
FE is missing |  | FIRE EXTINGUISER | MISSING
Site Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
MDP door need to fix |  | CIVIL_WORK | ACDB
FE is missing |  | FIRE EXTINGUISER | MISSING
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
Rectifier Batteries Installation Date tag is not available |  | LABELING | LABELING
FE IS MISSING |  | FIRE EXTINGUISER | MISSING
TN dummy is missing |  | DUMMY MISSING | DUMMY MISSING
FE is missing |  | FIRE EXTINGUISER | MISSING
Batteries Installation Date tag is not available |  | LABELING | LABELING
Delta Cabinet Battery backup banks faulty |  | BATTERY BACKUP | BATTERY BACKUP
FE need to replace |  | FIRE EXTINGUISER | EXPIRY
Delta cabinet cooling system is faulty |  | DELTA CABINET | AIR CONDITIONER
Delta cabinet Lock is faulty |  | DELTA CABINET | DOOR LOCK
OD Lighting is not working |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
Shelter door lock is faulty |  | CIVIL_WORK | SHELTER
A/C2 is not working | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
AC-2 IDU BLOWER MOTOR FAULTY(TOSHIBA)(TN SHELTER) | A/C ID unit Blower Motor Faulty | AIR_CONDITIONER | AIR CONDITIONER IDU
Emerson rectifier is working at site |  | DESIGN ISSUE | DESIGN ISSUE
Rectifier modules dummy missing |  | DUMMY MISSING | DUMMY MISSING
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Shelter cleaning is required |  | OTHERS | OTHERS
Site ID units cleaning is required | A/C ID units cleaning is required | AIR_CONDITIONER | AIR CONDITIONER IDU
rectifier modules dummy missing |  | DUMMY MISSING | DUMMY MISSING
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
OD greasing is required |  | OTHERS | OTHERS
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
AC1 PCB KIT FAULTY(2.5T GENERAL) | A/C PCB kit is faulty | AIR_CONDITIONER | PCB Kit
Site Battery backup Banks are weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Emerson rectifier is available at the site |  | DESIGN ISSUE | DESIGN ISSUE
Rectifier modules dummy missing |  | DUMMY MISSING | DUMMY MISSING
Site battery backup banks are fail | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
there is no safe pathway to reach up mountain tower antennas |  | DESIGN ISSUE | DESIGN ISSUE
ID lighting is not working |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
rectifier modules dummy missing |  | DUMMY MISSING | DUMMY MISSING
Site battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
FE is missing |  | FIRE EXTINGUISER | MISSING
Site battery backup banks are fail | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
FE is missing |  | FIRE EXTINGUISER | MISSING
Delta BTS cabinet cooling system is faulty |  | DELTA CABINET | AIR CONDITIONER
Delta cabinet filter need to replace and cabinet need to clean |  | DELTA CABINET | Filter
Logbook is missing |  | LOG BOOK | LOG BOOK
Site ID labeling is wrong and need to correct properly |  | LABELING | LABELING
FE is missing |  | FIRE EXTINGUISER | MISSING
Delta cabinet Filter is dirty and need to replace |  | DELTA CABINET | Filter
Cabinet Fire sensor need to fix properly |  | EXTERNAL ALARM | EXTERNAL ALARM
HOUSEKEEPING IS REQUIRED | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
BTS Foundation cracking |  | CIVIL_WORK | FOUNDATION
Site Antenna Sectors placed at non reachable locations over RT building / crane is required for any antenna maintenance action |  | DESIGN ISSUE | DESIGN ISSUE
FE is missing |  | FIRE EXTINGUISER | MISSING
Delta cabinet lock is faulty and cabinet cannot be open |  | DELTA CABINET | DOOR LOCK
housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
shelter roxtech sealing is required |  | OTHERS | OTHERS
Site battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
Logbook is missing |  | LOG BOOK | LOG BOOK
TN Dummy missing |  | DUMMY MISSING | DUMMY MISSING
Site battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Main gate padlock is missing | Site main gate padlock is missing | PADLOCK | PADLOCK
FE is missing |  | FIRE EXTINGUISER | MISSING
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Site battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
FE is missing |  | FIRE EXTINGUISER | MISSING
Tower legs grounding is missing |  | GROUNDING | TOWER
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Alarm is showing on rectifier controller |  | RECTIFIER | RECTIFIER
shelter roxtech sealing is required |  | OTHERS | OTHERS
rectifier controller is showing alarm |  | RECTIFIER | RECTIFIER
Rectifier dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Site battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
extra wooden box available in site premises |  | EXTRA MATERIAL | EXTRA MATERIAL
Rectifier modules dummy missing |  | DUMMY MISSING | DUMMY MISSING
Fiber cables arrangement is required | Fiber cables not arranged properly | CABLE DRESSING | Fiber
TN Dummy missing |  | DUMMY MISSING | DUMMY MISSING
FE is missing |  | FIRE EXTINGUISER | MISSING
FE is missing |  | FIRE EXTINGUISER | MISSING
FE is missing |  | FIRE EXTINGUISER | MISSING
Required New DC Air con Filter for Huawei BTS Cabinet | Delta Cabinet A/C Filter is damage | AIR_CONDITIONER | OD CABINET AIR CON
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
site main grounding is stolen |  | GROUNDING | GROUNDING
Site boundary wall cracking and seepage need to be fixed |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
tower legs grounding cables are missing |  | GROUNDING | TOWER
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
PDB is rusted |  | CIVIL_WORK | ACDB
FE is missing |  | FIRE EXTINGUISER | MISSING
Extra faulty disconnect batteries available in 2G cabinet |  | EXTRA MATERIAL | EXTRA MATERIAL
Site ID yellow label missing 2g cabinet 1 |  | LABELING | LABELING
Rectifier modules dummy missing in both two rectifiers |  | DUMMY MISSING | DUMMY MISSING
FE is missing |  | FIRE EXTINGUISER | MISSING
A/C2 is not working | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
ID Units cleaning is required | A/C ID units cleaning is required | AIR_CONDITIONER | AIR CONDITIONER IDU
Site Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
FE is expired Service date |  | FIRE EXTINGUISER | EXPIRY
rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Housekeeping is required due to Khareef weather | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
TN Dummy missing |  | DUMMY MISSING | DUMMY MISSING
Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
TN Dummy Missing |  | DUMMY MISSING | DUMMY MISSING
Expired |  | FIRE EXTINGUISER | EXPIRY
Require Arrangement | Cables not arranged properly | CABLE DRESSING | CABLE DRESSING
Battery Bank is faulty and damaged | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
All Ok |  | FIRE EXTINGUISER | EXPIRY
Cleaning required | A/C ID units cleaning is required | AIR_CONDITIONER | AIR CONDITIONER IDU
Extra Material At site |  | EXTRA MATERIAL | EXTRA MATERIAL
Need concrete base repair. |  | CIVIL_WORK | FOUNDATION
Major Housekeeping Required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Dummy Load Missing |  | DUMMY MISSING | DUMMY MISSING
Expired |  | FIRE EXTINGUISER | EXPIRY
Labeling Missing |  | LABELING | LABELING
Major rust- OT Site Gate |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Need Housekeeping- OT Site | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Foundation Issue- OT Tower |  | CIVIL_WORK | TOWER
Remote Battery need Replacement | One A/C remote control Batteries is missing | AIR_CONDITIONER | Remote Batteries
Battery Backup is zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Dummy Loads are missing |  | DUMMY MISSING | DUMMY MISSING
Missing FE |  | FIRE EXTINGUISER | MISSING
Expired |  | FIRE EXTINGUISER | EXPIRY
OT- painting Required |  | CIVIL_WORK | TOWER
Missing Dummy loads |  | DUMMY MISSING | DUMMY MISSING
Missing |  | FIRE EXTINGUISER | MISSING
Tn dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Power meter box is demolished | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
Main power supply phase cable is not protected properly and need to be fixed on priority.\r\n | Main Power Cables not arranged properly | CABLE DRESSING | Power Cable
Tn dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Pathway is completely Damaged from road to shelter-130m Length |  | CIVIL_WORK | PATHWAY DAMAGE
Dummy Missing |  | DUMMY MISSING | DUMMY MISSING
Non Huawei Rectifier |  | DESIGN ISSUE | DESIGN ISSUE
Missing |  | FIRE EXTINGUISER | MISSING
House keeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Outdoor light is not working |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
Tn dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Dummy Missing |  | DUMMY MISSING | DUMMY MISSING
Expired |  | FIRE EXTINGUISER | EXPIRY
Tn dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Fe is missing |  | FIRE EXTINGUISER | MISSING
Housekeeping required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Missing Dummy |  | DUMMY MISSING | DUMMY MISSING
Missing Dummy |  | DUMMY MISSING | DUMMY MISSING
Missing |  | FIRE EXTINGUISER | MISSING
Pathway damaged need to be Fixed |  | CIVIL_WORK | PATHWAY DAMAGE
Missing |  | FIRE EXTINGUISER | MISSING
Extra Materials exist at site |  | EXTRA MATERIAL | EXTRA MATERIAL
Aviation light system not working properly | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
Omantel cable ladder foundation broken and touching OO outdoor cabinet |  | OTHERS | OTHERS
Zero BB- batteries poles are rusty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Dummy Missing |  | DUMMY MISSING | DUMMY MISSING
Missing |  | LOG BOOK | LOG BOOK
Extra material on site (omantel site) |  | EXTRA MATERIAL | EXTRA MATERIAL
Dummy Missing |  | DUMMY MISSING | DUMMY MISSING
Shelter Body rusty |  | CIVIL_WORK | SHELTER
Dismantled V-sat dish in site arearn-Dismantled shelter inside site area |  | EXTRA MATERIAL | EXTRA MATERIAL
Tower is rusted |  | CIVIL_WORK | TOWER
Sector A antenna is hanged on the tower as upper bracket is broken |  | OTHERS | OTHERS
Tower ladder is broken |  | CIVIL_WORK | LADDER
Meter box Base/stand is broken | Power meter Box bases completely rusty-Damaged | CIVIL_WORK | ACDB
Expired |  | FIRE EXTINGUISER | EXPIRY
Missing |  | FIRE EXTINGUISER | MISSING
CLU Not working properly | HUW cabinet Door CLU Faulty | AIR_CONDITIONER | OD CABINET AIR CON
Gate Rusty Require painting |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
LTE TDD Cabinet battery backup is faulty |  | BATTERY BACKUP | BATTERY BACKUP
Expired |  | FIRE EXTINGUISER | EXPIRY
Missing |  | FIRE EXTINGUISER | MISSING
Fire panel battery is faulty |  | FIRE EQUIPMENT | FIRE EQUIPMENT
Missing |  | FIRE EXTINGUISER | MISSING
Gate major rust need Replacing |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Dummy Missing |  | DUMMY MISSING | DUMMY MISSING
All Columns have major rust and razor wire are damage |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Logbook missing |  | LOG BOOK | LOG BOOK
Greasing Required |  | OTHERS | OTHERS
Expired |  | FIRE EXTINGUISER | EXPIRY
Tn dummy is missing |  | DUMMY MISSING | DUMMY MISSING
battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra material are available at site Mount &amp; cable |  | EXTRA MATERIAL | EXTRA MATERIAL
Rectifier dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Fe is expired 26-07-2020 |  | FIRE EXTINGUISER | EXPIRY
Tn dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Battery backup is weak. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fe is missing |  | FIRE EXTINGUISER | MISSING
Main ac power meter door is damage | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Fe is missing |  | FIRE EXTINGUISER | MISSING
BTS door lock is damage |  | OTHERS | DOOR LOCK
Tn dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Fe is missing |  | FIRE EXTINGUISER | MISSING
Fe is missing |  | FIRE EXTINGUISER | MISSING
Rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
more than 100 meter walking due to pathway damage |  | CIVIL_WORK | PATHWAY DAMAGE
Labeling Missing |  | LABELING | LABELING
Missing label |  | LABELING | LABELING
Cables Arrangements required |  | CABLE DRESSING | CABLE DRESSING
Missing |  | FIRE EXTINGUISER | MISSING
Missing Lighting tube |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
Missing |  | FIRE EXTINGUISER | MISSING
Missing Dummy |  | DUMMY MISSING | DUMMY MISSING
Low performance batteries | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Pathway Has Damages |  | CIVIL_WORK | PATHWAY DAMAGE
No Grounding |  | GROUNDING | GROUNDING
Labeling Required |  | LABELING | LABELING
Fence Damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Missing |  | FIRE EXTINGUISER | MISSING
Ericsson CLU Faulty | Ericsson Outdoor Cabinet AC Faulty | AIR_CONDITIONER | OD CABINET AIR CON
Glass Broken |  | OTHERS | OTHERS
Dummy Missing |  | DUMMY MISSING | DUMMY MISSING
Expired |  | FIRE EXTINGUISER | EXPIRY
Missing |  | FIRE EXTINGUISER | MISSING
Pathway Damage |  | CIVIL_WORK | PATHWAY DAMAGE
Missing |  | FIRE EXTINGUISER | MISSING
Pathway Damage |  | CIVIL_WORK | PATHWAY DAMAGE
Missing |  | FIRE EXTINGUISER | MISSING
Expired |  | FIRE EXTINGUISER | EXPIRY
Missing-FE not available/not received from project team |  | FIRE EXTINGUISER | MISSING
Missing-Not Passed- Site ID not present on Outdoor cabinet from PT |  | LABELING | LABELING
Expired |  | FIRE EXTINGUISER | EXPIRY
Fire panel is having alarm |  | FIRE EQUIPMENT | FIRE EQUIPMENT
mobilized DG and fuel tank |  | EXTRA MATERIAL | EXTRA MATERIAL
Tower leg grounding cable is cut. |  | GROUNDING | TOWER
Tn dummy is missing |  | DUMMY MISSING | DUMMY MISSING
All are ok |  | FIRE EXTINGUISER | EXPIRY
Tn dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Tower leg grounding cable is cut |  | GROUNDING | TOWER
Tower leg grounding cable is cut |  | GROUNDING | TOWER
Rectifier dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Fe is missing |  | FIRE EXTINGUISER | MISSING
No proper pathway is available to reached antenna &amp; RRU maintenance |  | DESIGN ISSUE | DESIGN ISSUE
AC1 PCB KIT FAULTY(2.5T GENERAL) | A/C PCB kit is faulty | AIR_CONDITIONER | PCB Kit
Extra Materials at site |  | EXTRA MATERIAL | EXTRA MATERIAL
Missing |  | FIRE EXTINGUISER | MISSING
Missing |  | FIRE EXTINGUISER | MISSING
Missing |  | FIRE EXTINGUISER | MISSING
Missing Label |  | LABELING | LABELING
not working properly | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
Battery missing | One A/C remote control Batteries is missing | AIR_CONDITIONER | Remote Batteries
not exist |  | FIRE EXTINGUISER | EXPIRY
TN Dummy Missing |  | DUMMY MISSING | DUMMY MISSING
Expired |  | FIRE EXTINGUISER | EXPIRY
not working properly | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
Battery missing | One A/C remote control Batteries is missing | AIR_CONDITIONER | Remote Batteries
Ok |  | DUMMY MISSING | DUMMY MISSING
Rusty/ Need Painting |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Painting required |  | CIVIL_WORK | TOWER
Base Damage | Power meter Box bases completely rusty-Damaged | CIVIL_WORK | ACDB
Missing |  | FIRE EXTINGUISER | MISSING
not exist |  | FIRE EXTINGUISER | EXPIRY
Routing Issue |  | CABLE DRESSING | CABLE DRESSING
Expired |  | FIRE EXTINGUISER | EXPIRY
Some extra available |  | EXTRA MATERIAL | EXTRA MATERIAL
dummy load missing |  | DUMMY MISSING | DUMMY MISSING
Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Expired |  | FIRE EXTINGUISER | EXPIRY
Extra Rectifier exist |  | EXTRA MATERIAL | EXTRA MATERIAL
Transmission Shifted Via SIAE Link - Vast Dish need to Removed |  | EXTRA MATERIAL | EXTRA MATERIAL
Missing |  | FIRE EXTINGUISER | MISSING
Traffic shifter to MW- VSAT need to be removed |  | EXTRA MATERIAL | EXTRA MATERIAL
FE Missing |  | FIRE EXTINGUISER | MISSING
BBU3900 Not used and have missing dummy |  | DUMMY MISSING | DUMMY MISSING
Weak BB | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Gate Rusty |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra materials available at site |  | EXTRA MATERIAL | EXTRA MATERIAL
FE Expired |  | FIRE EXTINGUISER | EXPIRY
TN Missing Dummy Load |  | DUMMY MISSING | DUMMY MISSING
other vendor rectifier(s) available |  | DESIGN ISSUE | DESIGN ISSUE
Glass Broken |  | OTHERS | ACDB
DELTA FILTER NOT OK |  | DELTA CABINET | DELTA_FILTER
DELTA RECTIFIER CONTROLLER FAULTY(PSC3) |  | DELTA CABINET | RECTIFIER MODULE
WEAK BATTERY BACKUP(8 CELLS 180AH) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
DELTA FILTER NOT OK(3) |  | DELTA CABINET | DELTA_FILTER
DELTA FILTER NOT OK |  | DELTA CABINET | DELTA_FILTER
DELTA RECTIFIER CONTROLLER FAULTY(PSC3) |  | DELTA CABINET | RECTIFIER MODULE
EXTRA MATERIAL(DISMANTLED RF ANTENNAS) |  | EXTRA MATERIAL | EXTRA MATERIAL
WEAK BATTERY BACKUP(8 CELLS 180AH) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP(4 CELLS 100AH) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
ALARMS NOT CONFIGURED |  | DESIGN ISSUE | Design Issue
WEAK BATTERY BACKUP | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Shoto 190Ah 8 Battery cell faulty | Battery Backup is Zero/Dead | Battery Backup | BATTERY BACKUP
Shoto 190Ah 8 Battery cell faulty | Battery Backup is Zero/Dead | Battery Backup | BATTERY BACKUP
Shoto 190Ah 8 Battery cell faulty | Battery Backup is Zero/Dead | Battery Backup | BATTERY BACKUP
hybird DG got Faulty |  | DG ISSUES | DG
NO PATHWAY TO ACCESS SITE |  | CIVIL_WORK | PATHWAY DAMAGE
Tower Is rusted |  | CIVIL_WORK | TOWER
Tower Is rusted |  | CIVIL_WORK | TOWER
extra optix cabinet availble inside shelter |  | Extra Material | Extra Material
EXTRA MATERIAL AT SITE, 02 MW dishes |  | Extra Material | Extra Material
EXTRA MATERIAL AT SITE, Ericsson RBS2206 Cabinet in OSN Shelter |  | Extra Material | Extra Material
EXTRA MATERIAL(DISMANTLED ERICSSON PBC6500, MW DISH) |  | EXTRA MATERIAL | EXTRA MATERIAL
ID CAT LADDER STATUS NOK |  | CIVIL_WORK | CIVIL_WORK
EXTRA MATERIAL(DISMANTLED SHELTER) |  | EXTRA MATERIAL | EXTRA MATERIAL
ALARMS NOT CONFIGURED |  | DESIGN ISSUE | Design Issue
EXTRA MATERIAL(DISMANTLED SHELTER) |  | EXTRA MATERIAL | EXTRA MATERIAL
ALARMS NOT CONFIGURED |  | DESIGN ISSUE | Design Issue
ALARMS NOT CONFIGURED |  | DESIGN ISSUE | Design Issue
ALARMS NOT CONFIGURED |  | DESIGN ISSUE | Design Issue
A/C1 Compressor faulty shelter2 | A/C compressor is faulty | AIR_CONDITIONER | Compressor
8 batteries are faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Surface below fence foundation damaged by rain water |  | CIVIL_WORK | FOUNDATION
Tower foundation is cracked |  | CIVIL_WORK | Tower
battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
site main gate paint required |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
OG cabinet batteries need to replace |  | BATTERY BACKUP | BATTERY BACKUP
COW body is rusted |  | CIVIL_WORK | OTHERS
guy wire hooks are rusted |  | CIVIL_WORK | OTHERS
Site main gate angles are broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shelter paint required |  | CIVIL_WORK | Shelter
battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
No ladder to access antenna |  | DESIGN ISSUE | DESIGN ISSUE
week batery back up |  | BATTERY BACKUP | BATTERY BACKUP
emerson rectifier module faulty |  | Rectifier | Rectifier Module
week batery back up |  | BATTERY BACKUP | BATTERY BACKUP
Extra Metrial on the site |  | EXTRA MATERIAL | EXTRA MATERIAL
Extra material inside the shelter.mw dished |  | EXTRA MATERIAL | EXTRA MATERIAL
ETP48300C5A1 BATTERIES ARE WEAK. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
LIGHTINING ROD GROUNDING CABLE STOLEN-30M |  | GROUNDING | GROUNDING
LIGHTINING ROD GROUNDING CABLE STOLEN-30M |  | GROUNDING | GROUNDING
ETP48300C5A1 BATTERIES ARE WEAK. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
EXTRA MATERIAL AT SITE, SOME PROJECT MATERIALS LEFT OVER. |  | Extra Material | Extra Material
Mountain rocks are fell inside the compound and damaged wall a bit as well. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Missing FE |  | FIRE EXTINGUISER | EXPIRY
Missing |  | LOG BOOK | LOG BOOK
FE Missing |  | FIRE EXTINGUISER | EXPIRY
Missing |  | LOG BOOK | LOG BOOK
missing |  | FIRE EXTINGUISER | EXPIRY
FE Expired |  | FIRE EXTINGUISER | EXPIRY
ATN dummy Missing |  | DUMMY MISSING | DUMMY MISSING
Missing |  | LOG BOOK | LOG BOOK
FE Expired |  | FIRE EXTINGUISER | EXPIRY
Not working properly | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
Not exist from installation time |  | FIRE EXTINGUISER | EXPIRY
Not working properly | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
FE Missing |  | FIRE EXTINGUISER | EXPIRY
Housekeeping required due to Khareef weather | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
FE Missing |  | FIRE EXTINGUISER | EXPIRY
Housekeeping required de to kharif | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Missing FE |  | FIRE EXTINGUISER | EXPIRY
FE Missing |  | FIRE EXTINGUISER | EXPIRY
Greasing required |  | GROUNDING | ANTENNA GROUNDING
Missing |  | FIRE EXTINGUISER | EXPIRY
Dummy Missing |  | DUMMY MISSING | DUMMY MISSING
OSN Shelter body is rusted and damage |  | CIVIL_WORK | SHELTER
OSN shelter has Emerson rectifier |  | DESIGN ISSUE | DESIGN ISSUE
Expired FE |  | FIRE EXTINGUISER | EXPIRY
Rusty Gate |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Dismantle MW antennas available at site |  | EXTRA MATERIAL | EXTRA MATERIAL
Rod is ok tower grounding stolen |  | GROUNDING | GROUNDING
Nuts bolts are rusted need tower paint |  | CIVIL_WORK | TOWER
FE Missing |  | FIRE EXTINGUISER | EXPIRY
FE Missing |  | FIRE EXTINGUISER | EXPIRY
FE Expired |  | FIRE EXTINGUISER | EXPIRY
Missing FE |  | FIRE EXTINGUISER | EXPIRY
Need to remove some sand to be accessible |  | CIVIL_WORK | Sand
Need Housekeeping due to Khareef weather | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Missing FE from Installation Time |  | FIRE EXTINGUISER | EXPIRY
DG and Tanks Not Grounded |  | DG ISSUES | DG ISSUES
Missing FE |  | FIRE EXTINGUISER | EXPIRY
FE is Not Available |  | FIRE EXTINGUISER | EXPIRY
Rooftop no ladder to access antenna- temporary scaffolding available |  | DESIGN ISSUE | DESIGN ISSUE
FE not Exist |  | FIRE EXTINGUISER | EXPIRY
FE Missing from Installation Time |  | FIRE EXTINGUISER | EXPIRY
Not Grounded |  | DG ISSUES | DG ISSUES
FE Expired |  | FIRE EXTINGUISER | EXPIRY
Earth Bar Stolen |  | GROUNDING | GROUNDING
FE Missing |  | FIRE EXTINGUISER | EXPIRY
DG Not grounded |  | DG ISSUES | DG ISSUES
TN has missing dummies |  | DUMMY MISSING | DUMMY MISSING
Fe not Exist |  | FIRE EXTINGUISER | EXPIRY
FE not exist |  | FIRE EXTINGUISER | EXPIRY
FE not Exist |  | FIRE EXTINGUISER | EXPIRY
FE Not exist |  | FIRE EXTINGUISER | EXPIRY
Rectifier dummies missing |  | DUMMY MISSING | DUMMY MISSING
FE Expired |  | FIRE EXTINGUISER | EXPIRY
FE not exist |  | FIRE EXTINGUISER | EXPIRY
FE Not exist |  | FIRE EXTINGUISER | EXPIRY
OD shelter Lighting is missing |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
FE Missing |  | FIRE EXTINGUISER | EXPIRY
FE needle is not in green area- Seems expired |  | FIRE EXTINGUISER | EXPIRY
FE Missing |  | FIRE EXTINGUISER | EXPIRY
FE expired |  | FIRE EXTINGUISER | EXPIRY
FE expired |  | FIRE EXTINGUISER | EXPIRY
Site Area is sandy and need walls instead of Wire Mesh |  | DESIGN ISSUE | DESIGN ISSUE
FE Expired |  | FIRE EXTINGUISER | EXPIRY
Dummy Load Missing |  | DUMMY MISSING | DUMMY MISSING
Shoto Batteries seems not Healthy- installed |  | BATTERY BACKUP | BATTERY BACKUP
Site is in very Narrow Area and exit way is not clear- | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
EXTRA MATERIAL AT SITE, METRO-3100 |  | Extra Material | Extra Material
OSN SHELTER, EMERSON POWER SYSTEM BATTERIES ARE WEAK. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
EXTERNAL ALARMS ARE PATCHED BUT NOT CONFIGURED IN TN6P SAU USER I/O AUX, THEREFORE NONE OF ALARM IS REPORTING TO NOC. |  | DESIGN ISSUE | DESIGN ISSUE
ETP48300C5A1 BATTERIES ARE FAULTY/DEAD. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
LIGHTINING ROD GROUNDING CABLE IS BROKEN IN THE MIDDLE. |  | GROUNDING | GROUNDING
APM30H BATTERIES ARE FAULTY. |  | BATTERY BACKUP | BATTERY BACKUP
NO SAFE LADDER IS AVAILABLE TO ACCESS AIRCONS OD UNITS. |  | DESIGN ISSUE | DESIGN ISSUE
MAIN GATE IS DAMAGED, 1 SIDE IS BROKEN, CAN'T BE LOCKED. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
ETP48300C5A1 BATTERIES ARE FAULTY/DEAD. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP WEAK | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra Cabinet At site |  | EXTRA MATERIAL | EXTRA MATERIAL
TDD rectifier both batery bank faulty |  | BATTERY BACKUP | BATTERY BACKUP
2G 3G week batery back up |  | BATTERY BACKUP | BATTERY BACKUP
LIGHTINING ROD GROUNDING CABLE IS BROKEN IN THE MIDDLE. |  | GROUNDING | GROUNDING
EXTRA MATERIAL AT SITE, OPTIX METRO 3100. |  | Extra Material | Extra Material
EXTRNAL ALARMS ARE NOT PATCHED AND CONFIGURED, THEREFORE NONE OF ALARMS ARE REPORTING TO NOC. |  | DESIGN ISSUE | DESIGN ISSUE
EMERSON NETWORK POWER SYSTEM BATTERIES ARE FAULTY. |  | BATTERY BACKUP | BATTERY BACKUP
EXTRA MATERIAL AT SITE, UPM POWER SUPPLY WITH BATTERIES IN OSN RACK. |  | Extra Material | Extra Material
LIGHTINING ROD GROUNDING CABLE IS BROKEN IN THE MIDDLE. |  | GROUNDING | GROUNDING
ETP48300C5A1 BATTERIES ARE FAULTY/DEAD. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
EXTRA MATERIAL AT SITE, DISMANTLED APM30 CABINETS, UPM, DISH, BATTERIES etc. |  | Extra Material | Extra Material
ETP48300C5A1 BATTERIES ARE FAULTY/DEAD. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
TP48400 Rect battery bank week |  | Battery Backup | BATTERY BACKUP
Extra Metrial Out side shalter |  | Extra Material | Extra Material
extra material on site(combiner etc) |  | Extra Material | Extra Material
tower main grounding cable and lightning arrester missing. |  | Grounding | Grounding
tower gorunding missing |  | Grounding | Grounding
wimax and 2G/3G Rectifire battery week | TDD/WiMax Battery Backup is Weak | Battery Backup | BATTERY BACKUP
extra material in side shelter 1(metro cabinet) and in shelter 2 breakers. |  | EXTRA MATERIAL | EXTRA MATERIAL
EXTRA MATERIAL METRO in site POWER ALREADY OFF and 2G 1 RRU |  | EXTRA MATERIAL | EXTRA MATERIAL
extra 6m pole avail on site |  | Extra Material | Extra Material
Site Pathway is damaged from bottom side around 20M |  | CIVIL_WORK | PATHWAY DAMAGE
FE is missing |  | FIRE EXTINGUISER | EXPIRY
&bull; BBU located inside store room and extra material placed at site like water bottles packet (Belongs to building) | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Site Battery Backup is zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Electric poles beside boundary wall and housekeeping is required /OT is a host | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Extra Wimax Rack available in shelter |  | EXTRA MATERIAL | EXTRA MATERIAL
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Extra material PBC6500 cabinet |  | EXTRA MATERIAL | EXTRA MATERIAL
Emerson rectifier is in operational at the shelter |  | DESIGN ISSUE | DESIGN ISSUE
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Main Gate totally rusted and damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site fence razor is rusted and damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra home assets stored at site premises /These belong to Hotel |  | EXTRA MATERIAL | EXTRA MATERIAL
Tower lightning rod cable is missing |  | GROUNDING | GROUNDING
rectifier module dummy missing |  | DUMMY MISSING | DUMMY MISSING
IBS room Fiber cables need to be arranged properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Fiber cables arrangement is required | Fiber cables not arranged properly | CABLE DRESSING | Fiber
Site battery backup is zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Site pathway is damage approximately 120-150 meter |  | CIVIL_WORK | PATHWAY DAMAGE
Power source is DG. CAT and Two phases are missing from DG source |  | DG ISSUES | DG ISSUES
AC1 PCB KIT FAULTY(2.5T GENERAL) | A/C PCB kit is faulty | AIR_CONDITIONER | PCB Kit
pathway is damaged at multiple areas \\\\ Site located on big hill around 3km |  | CIVIL_WORK | PATHWAY DAMAGE
snake found at outdoor ac area and house keeping required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
one delta rectifier module not working |  | Delta Cabinet | RECTIFIER MODULE
Rectifier dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Delta filter need to replace |  | Delta Cabinet | Filter
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
Site Battery backup banks are weak and need to replace | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Tower painting is required |  | CIVIL_WORK | TOWER
Shelter Lock is broken |  | CIVIL_WORK | SHELTER DOOR
A/Cs OD Units are rusted | Both A/C ODU is Rusty | AIR_CONDITIONER | AIR CONTIONER ODU
Fire control panel is having alarm and not working |  | FIRE EQUIPMENT | Fire Panel
Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
FE is missing |  | FIRE EXTINGUISER | EXPIRY
FE is missing |  | FIRE EXTINGUISER | EXPIRY
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Site Batteries installation date tag is missing |  | LABELING | LABELING
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
FE is missing |  | FIRE EXTINGUISER | EXPIRY
External Fuel tank is rusted |  | DG ISSUES | DG ISSUES
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
ETP48300C5A1 BATTERIES ARE FAULTY/DEAD. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
LIGHTINING ROD GROUNDING CABLE IS STOLEN. |  | GROUNDING | GROUNDING
EXTRA MATERIAL AT SITE, VSAT DISH. |  | Extra Material | Extra Material
ETP48300C5A1 BATTERIES ARE FAULTY/DEAD. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
EXTRA MATERIAL AT SITE, VSAT DISH. |  | Extra Material | Extra Material
MAIN GATE IS DAMGED, UNABLE CLOSE. |  | CIVIL_WORK | Main Gate
EXTRA MATERIAL AT SITE, VSAT DISH. |  | Extra Material | Extra Material
ETP48300C5A1 BATTERIES ARE WEAK. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
LIGHTINING ROD GROUNDING CABLE IS STOLEN. |  | GROUNDING | GROUNDING
EXTRA MATERIAL AT SITE, 02 MW DISHES. |  | Extra Material | Extra Material
ETP48300C5A1 BATTERIES ARE WEAK. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
ETP48300C5A1 BATTERIES ARE WEAK. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
ETP48300C5A1 BATTERIES ARE WEAK. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
major housekeeping required | Site Housekeeping is required | Housekeeping | Housekeeping
All sectors grounding cble cut from pole to main bus bar |  | Grounding | Grounding
week batery backup |  | BATTERY BACKUP | BATTERY BACKUP
week batery backup |  | BATTERY BACKUP | BATTERY BACKUP
Tower paint is required |  | CIVIL_WORK | TOWER
T Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Meter box door glass is broken | Power meter Box glass missing | CIVIL_WORK | ACDB
FE is missing |  | FIRE EXTINGUISER | EXPIRY
TN power redundancy cable is missing |  | DUMMY MISSING | DUMMY MISSING
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Only one DC supply to TN/No power redundancy |  | DUMMY MISSING | DUMMY MISSING
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Site Battery backup banks are Zero and need to to replace | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
FE is missing |  | FIRE EXTINGUISER | EXPIRY
A/C2 PCB Kit is Faulty | A/C PCB kit is faulty | AIR_CONDITIONER | PCB Kit
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Fire control panel is faulty |  | FIRE EQUIPMENT | Fire Panel
Indoor shelter light is faulty |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
A/C2 PCB kit is faulty | A/C PCB kit is faulty | AIR_CONDITIONER | PCB Kit
FE is missing |  | FIRE EXTINGUISER | EXPIRY
One Battery string is zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Fire control panel is faulty |  | FIRE EQUIPMENT | Fire Panel
DG and external tank require cleaning |  | DG ISSUES | DG ISSUES
Tower base is cracked |  | CIVIL_WORK | FOUNDATION
Site Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
OT is a host /Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Main gate lock is not available / OT is a host | Site main gate padlock is missing | PADLOCK | PADLOCK
RSL is very High |  | OTHERS | Other
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
3 Rectifier modules are having alarms |  | RECTIFIER | RECTIFIER MODULE
Need refilling concrete inside boundary |  | CIVIL_WORK | COMPOUND
Lightning rod cable is missing |  | GROUNDING | GROUNDING
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
FE is missing |  | FIRE EXTINGUISER | EXPIRY
One Solar Plate damage |  | OTHERS | Other
Tower ladder base foundation is damage |  | CIVIL_WORK | FOUNDATION
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Shelter Main grounding cable is Cut |  | GROUNDING | GROUNDING
Lightning rod cable is cut |  | GROUNDING | GROUNDING
Indoor lighting is not working |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Site battery backup is zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Extra brackets placed under the COW |  | EXTRA MATERIAL | EXTRA MATERIAL
FE is missing |  | FIRE EXTINGUISER | EXPIRY
There is no Boundary Fence installed at the site |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Site Major housekeeping is required / RT Site and building residences storing extra material surrounding shelter | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
OD IF cables and RT fiber cables need to arrange and protect properly | IF cables not arranged properly | CABLE DRESSING | IF
OD lighting is not working |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
Shelter roxtech sealing is required |  | OTHERS | Other
Site battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
RT Ladder foundation is damaged |  | CIVIL_WORK | RT Ladder
ID lighting system need to fix |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
Shelter roxtech sealing is required |  | OTHERS | Other
ID lighting system need to fix |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
RT BTS room door latch need to fix |  | OTHERS | Other
Shelter roxtech sealing is required |  | OTHERS | Other
A/C1 is not working | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Rectifier dummy missing |  | DUMMY MISSING | DUMMY MISSING
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
Some Poles main grounding cables are cut |  | GROUNDING | GROUNDING
Site Battery backup is faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
PDB cables sealing need to fix |  | OTHERS | Other
OD cabinet Air con Compressor is faulty | HUW cabinet Door CLU Faulty | AIR_CONDITIONER | OD CABINET AIR CON
Extra materials present at COW site |  | EXTRA MATERIAL | EXTRA MATERIAL
COW Tower is rusted / located at Mutrah beach |  | CIVIL_WORK | TOWER
COW Lighting system is not working |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
One PSU is faulty |  | RECTIFIER | RECTIFIER MODULE
Rectifier controller is showing Phase 2 is NA . |  | RECTIFIER | RECTIFIER
some battery cells physical condition is not OK | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
DP box proper sealing is required |  | OTHERS | Other
Main gate padlock is missing &amp; COW Cage lock is also faulty | Site main gate padlock is missing | PADLOCK | PADLOCK
Main gate and boundary fence is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
RT site access is unsafe at all as team should climb one external spiral ladder then cross to 2nd building through woody horizontal ladder placed in between the two separated buildings ( i had special access permission from inside through building internal private stairs ) |  | DESIGN ISSUE | DESIGN ISSUE
Some OD cables need to arrange properly and extra cables need to be dismantled | OD cable not arranged properly | CABLE DRESSING | CABLE DRESSING
RT portable woody ladder need to replace by new safe fixed ladder to reach RT safely |  | DESIGN ISSUE | DESIGN ISSUE
Phase1 - 2-3 Failure alarm is presented on 5G cabinet rectifier controller &amp; HW fault alarm is showing on BTS rectifier controller |  | RECTIFIER | RECTIFIER ALARMS
Rectifier modules Dummy missing in 5G cabinet |  | DUMMY MISSING | DUMMY MISSING
BTS Cabinet Battery backup is dead and need to replace | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
PD Box sealing and rust removal action is required |  | OTHERS | Other
OD Delta cabinet cooling system is faulty |  | DELTA CABINET | AIR CONDITIONER
OD Delta cabinet filter need to replace |  | DELTA CABINET | Delta_Filter
High temperature detector is faulty | High temperature detector is faulty | AIR_CONDITIONER | sensor
Rectifier dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Some alarms connected Manually |  | EXTERNAL ALARM | EXTERNAL ALARM
Shelter main grounding cable is cut |  | GROUNDING | GROUNDING
OD feeder cables need to arrange properly | OD cable not arranged properly | CABLE DRESSING | CABLE DRESSING
AC1 PCB KIT FAULTY(2.5T GENERAL) | A/C PCB kit is faulty | AIR_CONDITIONER | PCB Kit
Rectifier dummy is missing |  | DUMMY MISSING | DUMMY MISSING
2 battery cells are weak out of 16 cells | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
RT OD Cable tray Cover need to be fixed properly |  | CIVIL_WORK | CABLE TRAY
2 Battery cells poles need to clean |  | BATTERY BACKUP | BATTERY BACKUP
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
OD Delta Cabinet lower part cover need to fix properly |  | DELTA CABINET | Other
5G cabinet fan and cooling system is not working | HUW cabinet Door CLU Faulty | AIR_CONDITIONER | OD CABINET AIR CON
soil treatment is required under the shelter |  | CIVIL_WORK | COMPOUND
Tower main grounding cable is cut |  | GROUNDING | GROUNDING
Tower feeder need to arrange properly on the tower | Tower Ladder Cables Need Arrangement | CABLE DRESSING | Tower
Roxtech sealing is required |  | OTHERS | Other
AC1 OD unit frame need to fix properly | OD unit - frame not fixed properly | AIR_CONDITIONER | AIR CONTIONER ODU
Prim DG main power supply cable not routed and protected properly |  | DESIGN ISSUE | DESIGN ISSUE
Prim DG external fuel tank was having leakage spot and need to clean |  | DG ISSUES | DG ISSUES
Part of DG canopy need to be fixed |  | DG ISSUES | DG ISSUES
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Site Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
FE is missing |  | FIRE EXTINGUISER | EXPIRY
POWER METER BOX GLASS IS BROKEN AND COVERED BY TAPE | Power meter Box glass missing | CIVIL_WORK | ACDB
Site main gate and fence is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
power meter box is rusted | Power meter Box completely rusty-Damages- Need Replace | CIVIL_WORK | ACDB
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Aviation light board is burnt | Aviation light panel Faulty/damaged | AVIATION_LIGHT | AVIATION_LIGHT
AC1 is not working due to Freon gas leakage | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
FE is missing |  | FIRE EXTINGUISER | EXPIRY
BTS Room door lock is faulty |  | OTHERS | Other
AC1 is working on Hand mode and mode and AC2 is working on Auto Mode | One A/C is working on manual mode | AIR_CONDITIONER | Hand Mode
FE service sticker is missing |  | FIRE EXTINGUISER | EXPIRY
Rectifier module dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Site hill pathway repairing is required |  | CIVIL_WORK | PATHWAY DAMAGE
Extra cable tray parts placed next to shelte+ TN2P kit |  | EXTRA MATERIAL | EXTRA MATERIAL
Power meter box door is not closed |  | OTHERS | Other
PDB need to fix properly |  | OTHERS | Other
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
OD Delta cabinet handheld lock is faulty |  | DELTA CABINET | DOOR LOCK
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
Delta cabinet filter need to replace |  | DELTA CABINET | Delta_Filter
Delta cabinet door lock is faulty |  | DELTA CABINET | DOOR LOCK
OD BTS handle lock is faulty |  | OTHERS | Other
FE is missing |  | FIRE EXTINGUISER | EXPIRY
FE is missing |  | FIRE EXTINGUISER | EXPIRY
PDB is rusty |  | OTHERS | Other
Main gate lock is missing -OT is a host | Site main gate padlock is missing | PADLOCK | PADLOCK
FE is missing |  | FIRE EXTINGUISER | EXPIRY
ETP48300C5A1 BATTERIES ARE WEAK/DEAD Backup. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
EXTRA MATERIAL AT SITE, VSAT DISH WITH ITS NE. |  | Extra Material | Extra Material
EXTERNAL ALARMS ARE NOT PATCHED/CONFIGURED ON RNN BBU, DESIGN ISSUE. |  | DESIGN ISSUE | DESIGN ISSUE
ETP48300C5A1 BATTERIES ARE WEAK/DEAD Backup. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
EXTRA MATERIAL AT SITE, 02 MW DISHES, TN2P. |  | Extra Material | Extra Material
FENCE HAS BEEN FALLEN TO GROUND/COLLAPSED. MAIN GATE IS DAMAGED, BROKEN. SITE SECURITY IS COMPROMISED. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
ETP48300C5A1 BATTERIES ARE WEAK. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
FENCE HAS BEEN FALLEN TO GROUND/COLLAPSED. GRID WIRES ARE LOSE. |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
OUTDOOR APM30H BATTERIES ARE WEAK. | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Extra material(ODF RACK) |  | Extra Material | Extra Material
BB IS WEAK(LI BATTERY 150AH DUE TO CYCLONE) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BB DUE HIGH LOAD, NEED TO SHIFT LOAD TO 2ND RECTIFIER | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
FENCE DAMAGED(OT HOST) |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
WEAK BATTERY BACKUP | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
TOWER LIGHTNING PROTECTOR GND STOLEN(25M) |  | GROUNDING | GROUNDING
Extra material(MW MOUNT) |  | Extra Material | Extra Material
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
CP METER BOX DAMAGED(DUE TO CYCLONE) |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
AC1 not working,general | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
AC FILTER FAULTY |  | DELTA CABINET | Filter
TDD Battery bank is dead | TDD/WiMax Battery Backup is Zero/Dead | BATTERY BACKUP | TDD/WiMax
ac control pannal faulty | A/C CONTROL Panel is FAULTY | AIR_CONDITIONER | Control Panel
ac 1, general,compresor faulty | A/C compressor is faulty | AIR_CONDITIONER | Compressor
EXTRA MATERIAL AT SITE. CABLES, BOXES etc. |  | Extra Material | Extra Material
ETP48300C5A1 BATTERIES ARE WEAK/DEAD Backup. | BB is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
EXTRA MATERIAL AT SITE, VSAT DISH WITH ITS NE. |  | Extra Material | Extra Material
Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Delta cabinet AC is Faulty. |  | DELTA CABINET | AIR_CONDITIONER
DELTA FILTER NOT OK |  | DELTA CABINET | DELTA_FILTER
housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
DELTA FILTER NOT OK |  | DELTA CABINET | DELTA_FILTER
EXTRA MATERIAL(DISMANTLED 2 RF ANTENNA) |  | EXTRA MATERIAL | EXTRA MATERIAL
housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
DELTA FILTER NOT OK(BOTH CABINET) |  | DELTA CABINET | DELTA_FILTER
EXTRA MATERIAL(DISMANTLED MW DISH) |  | EXTRA MATERIAL | EXTRA MATERIAL
Tower lightning protector rod ground cable missing(50M) |  | GROUNDING | GROUNDING
ACDB cover not installed due to wrong installation of fsu CT |  | Wrong Installation | Wrong Installation
EXTRA MATERIAL(BELONGST TO PT) |  | EXTRA MATERIAL | EXTRA MATERIAL
Battery backup is weak( 4 CELLS* 190AH) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
housekeeping is required (BIG TREE BLOCKING MAIN GATE) | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
CP METER BOX DAMAGED |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
EXTRA MATERIAL(DISMANTLED AVR IN GUL SHELTER) |  | EXTRA MATERIAL | EXTRA MATERIAL
fence damaged due to land sliding |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
There is no access to tower(at hilltop) |  | DESIGN ISSUE | Design Issue
Wall broken due to land sliding |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Extra material(vsat modem,dish,inverter) |  | Extra Material | Extra Material
Weak bb(8 cells) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra material(vsat modem,dish,inverter) |  | Extra Material | Extra Material
Extra material(vsat modem,dish,inverter) |  | Extra Material | Extra Material
TN Dummy is missing -no traffic on TN |  | DUMMY MISSING | DUMMY MISSING
TDD Cabinet battery backup is Zero |  | BATTERY BACKUP | BATTERY BACKUP
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
Site Main gate is rusted and broken |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
NPT Tower need to paint |  | CIVIL_WORK | TOWER
Battery rack is rusted |  | OTHERS | OTHER
PDB is rusted |  | OTHERS | OTHER
fence and main gate rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
OD Delta Cabinet AC is faulty |  | DELTA CABINET | AIR CONCITIONER
Cabinet is fully dusted and delta filter need to replace |  | DELTA CABINET | Filter
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Tower Main grounding cable is missing |  | GROUNDING | GROUNDING
Emergency light is not working |  | Emergency Light | Emergency Light
Minor housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Lightning rod cable is stolen |  | GROUNDING | GROUNDING
Tower grounding cables stolen |  | GROUNDING | GROUNDING
FE is missing |  | FIRE EXTINGUISER | EXPIRY
2G/3g Cabinet cooling system is faulty | BTS Cooling system is faulty | AIR_CONDITIONER | OD CABINET AIR CON
Some minor alarms observed on rectifier controller |  | RECTIFIER | RECTIFIER ALARMS
Site Battery backup banks are faulty |  | BATTERY BACKUP | BATTERY BACKUP
FE is missing |  | FIRE EXTINGUISER | EXPIRY
BTS Cooling system is faulty | BTS Cooling system is faulty | AIR_CONDITIONER | OD CABINET AIR CON
Site Battery backup is zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
FE is missing |  | FIRE EXTINGUISER | EXPIRY
alarms observed on rectifier controller |  | DUMMY MISSING | DUMMY MISSING
BTS Cooling system is faulty | BTS Cooling system is faulty | AIR_CONDITIONER | OD CABINET AIR CON
OD cabinet door lock is faulty |  | OTHERS | DOOR LOCK
All Tower legs and tower main ground are missing |  | GROUNDING | GROUNDING
One customer link power is connected to AC directly |  | DESIGN ISSUE | DESIGN ISSUE
Distribution penal lock is broken |  | OTHERS | OTHER
BTS Air con system is faulty |  | DELTA CABINET | AIR CONCITIONER
Delta Aircon Filter damage and faulty |  | DELTA CABINET | Filter
Delta outdoor cabinet door lock broken and damage |  | DELTA CABINET | DOOR LOCK
External alarms are not working because of faulty rectifier PSC3 |  | EXTERNAL ALARM | EXTERNAL ALARM
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
No backup for Hybrid BB so need replacement on priority | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
FE is missing |  | FIRE EXTINGUISER | EXPIRY
External Tank base foundation is not available |  | DG ISSUES | DG ISSUES
Hybrid DG is not working on Auto mode due to Hybrid BB zero |  | DG ISSUES | DG ISSUES
FE is missing |  | FIRE EXTINGUISER | EXPIRY
DG and external tank not grounded |  | DG ISSUES | DG ISSUES
Fiber cable safe routing is required on priority | Fiber cables not arranged properly | CABLE DRESSING | Fiber
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
Shelter main Ground cable is missing |  | GROUNDING | GROUNDING
Shelter door lock is faulty |  | CIVIL_WORK | SHELTER
Shelter roof sealing is required |  | CIVIL_WORK | SHELTER
Ac1 is auto not producing cooling\r\nAc2 is on hand mode | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
door Latch broken /padlock missing at site |  | CIVIL_WORK | SHELTER
Rectifier dummy missing |  | DUMMY MISSING | DUMMY MISSING
FE is missing |  | FIRE EXTINGUISER | EXPIRY
extra material at site (wimax cabinet frame- wimax antenna- jumpers) |  | EXTRA MATERIAL | EXTRA MATERIAL
one tube light not working |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
AC1 PCB kit is faulty | A/C PCB kit is faulty | AIR_CONDITIONER | PCB Kit
Rectifier dummy is missing |  | DUMMY MISSING | DUMMY MISSING
TDD having zero battery backup but Other technologies having medium backup |  | BATTERY BACKUP | BATTERY BACKUP
Fire extinguisher Service label is missing |  | FIRE EXTINGUISER | EXPIRY
Site main earth cable is missing |  | GROUNDING | GROUNDING
OD cables arrangement is required | OD cable not arranged properly | CABLE DRESSING | CABLE DRESSING
BTS room door lock and clutch are faulty |  | CIVIL_WORK | SHELTER
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
BTS room is having major seepage and need civil action |  | CIVIL_WORK | SHELTER
One AC is faulty | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
TDD cabinet is having zero battery |  | BATTERY BACKUP | BATTERY BACKUP
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
One rectifier module is faulty |  | DELTA CABINET | RECTIFIER MODULE
Delta cabinet filter is faulty and need to replace |  | DELTA CABINET | AIR CONDITIONER
Some ID &amp; OD ground cables are cut |  | GROUNDING | GROUNDING
OD fiber cables not protected and Fiber junction box need sealing | Fiber cables not arranged properly | CABLE DRESSING | Fiber
BTS Room roof sealing is required ( Big roof area ) and walls seepage is there too |  | CIVIL_WORK | SHELTER
One AC is faulty | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Rectifier module dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Site Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shelter body is rusted |  | CIVIL_WORK | SHELTER
FE is missing |  | FIRE EXTINGUISER | EXPIRY
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
FE is missing |  | FIRE EXTINGUISER | EXPIRY
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
fence foundation damaged |  | CIVIL_WORK | Foundation
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Site Battery Backup Banks are Zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Site Major housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Lightning rod cable is missing |  | GROUNDING | GROUNDING
Meter box glass is broken |  | CIVIL_WORK | Main DB
Site main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site Major housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Hybrid DG is on Manual Mode |  | DG ISSUES | DG ISSUES
FE sticker is expired service date |  | FIRE EXTINGUISER | EXPIRY
Extra materials available at site premises |  | EXTRA MATERIAL | EXTRA MATERIAL
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
One Battery cell cover is missing |  | BATTERY BACKUP | BATTERY BACKUP
Extra Small TN Cabinet |  | EXTRA MATERIAL | EXTRA MATERIAL
FE is expired |  | FIRE EXTINGUISER | EXPIRY
FE is missing since site integrated |  | FIRE EXTINGUISER | EXPIRY
Site Main gate is totally rusted and damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site Fence is completely rusted and damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
FE is missing since site was integrated |  | FIRE EXTINGUISER | EXPIRY
FE is missing since site had integrated |  | FIRE EXTINGUISER | EXPIRY
Site main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
FE is missing since site integration |  | FIRE EXTINGUISER | EXPIRY
Site Main gate is damaged / There is no gate |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
aviation light is not working | Aviation light panel Faulty/damaged | AVIATION_LIGHT | TOWER
Tower paint is required |  | CIVIL_WORK | TOWER
cable tray is damaged |  | CIVIL_WORK | CABLE TRAY
PDB is rusted |  | OTHERS | OTHER
Site fence is rusted and damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
FE is missing |  | FIRE EXTINGUISER | EXPIRY
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
FE is missing |  | FIRE EXTINGUISER | EXPIRY
DG and external tank not grounded |  | DG ISSUES | DG ISSUES
Site major housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Cable tray support foundation is cracked |  | CIVIL_WORK | CABLE TRAY
Shelter floor is not leveled |  | CIVIL_WORK | FOUNDATION
Emerson rectifier is working at the site |  | DESIGN ISSUE | DESIGN ISSUE
Rectifier modules Dummies are missing |  | DUMMY MISSING | DUMMY MISSING
one battery cell in two different rectifiers are fail |  | BATTERY BACKUP | BATTERY BACKUP
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Site Battery banks are faulty | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Feeder cables dressing is required |  | CABLE DRESSING | CABLE DRESSING
A/C1 is not working and water leakage is running | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Emerson rectifier is there |  | DESIGN ISSUE | DESIGN ISSUE
Dummies are missing |  | DUMMY MISSING | DUMMY MISSING
Emerson Battery backup is fail | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
Tower lower section guy wire is cut |  | CIVIL_WORK | TOWER
Site Battery backup banks are fail | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
Delta filter cabinet need to replace |  | DELTA CABINET | AIR CONCITIONER
OD BTS Delta cabinet door lock is faulty |  | DELTA CABINET | DOOR LOCK
Lightning rod cable is cut |  | GROUNDING | GROUNDING
Tower paint is required |  | CIVIL_WORK | TOWER
Birds home created on tower RRU |  | OTHERS | OTHER
Shelter is rusted and body has impacted by cyclone -Site is located in Cyclone highly impacted area near to the sea |  | CIVIL_WORK | SHELTER
AC DRAINAGE CHOCKED | AC DRAINAGE CHOCKED | AIR_CONDITIONER | DRAINAGE
power meter box need cleaning and rust removal after cyclone impact |  | CIVIL_WORK | Main DB
2nd rectifier battery string got faulty because of the cyclone | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
site boundary fence - fence rod and razor wire are rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Fire control panel got faulty |  | FIRE EQUIPMENT | Fire Panel
SDMO Generator got faulty due to cyclone |  | DG ISSUES | DG ISSUES
Site main gate is completely damaged and fence is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shelter door lock is faulty |  | CIVIL_WORK | SHELTER
Shelter body is rusted |  | CIVIL_WORK | SHELTER
Roxtech sealing is required |  | CIVIL_WORK | SHELTER
AC 2 is not producing cooling. | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Tower paint is required |  | CIVIL_WORK | TOWER
Roxtech sealing is required |  | CIVIL_WORK | OTHER
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Fire control panel is not working |  | FIRE EQUIPMENT | Fire Panel
Minor housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Shelter door lock is faulty |  | CIVIL_WORK | SHELTER
shelter body has rusted parts |  | CIVIL_WORK | SHELTER
ID units filters cleaning is required | A/C ID units cleaning is required | AIR_CONDITIONER | AIR CONDITIONER IDU
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Dismantle Ericsson Rectifier still at site after hybrid swap |  | EXTRA MATERIAL | EXTRA MATERIAL
Aviation light is not installed since site integration | Aviation light system need to be installed | AVIATION_LIGHT | TOWER
FE service sticker is missing |  | FIRE EXTINGUISER | EXPIRY
DG canopy is rusted |  | DG ISSUES | DG ISSUES
Extra material(antenna base frame) |  | EXTRA MATERIAL | EXTRA MATERIAL
DELTA AC is faulty. |  | DELTA CABINET | AIR_CONDITIONER
House keeping is required TO ACCESS CP METER | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Ac 1 is working in hand \r\nAc2 is Off | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Extra material(Dismantled cabinet-cyclone affected site) |  | EXTRA MATERIAL | EXTRA MATERIAL
House keeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Rectifier modules dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Site Battery Backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Cable tray is having minor rust |  | CIVIL_WORK | CABLE TRAY
Shelter body is rusted (from back side 20%) |  | CIVIL_WORK | SHELTER
Meter box is rusted |  | CIVIL_WORK | Main DB
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Main gate is rusted and need paint |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Engine oil leakage available |  | DG ISSUES | DG ISSUES
DG and External tank are not grounded |  | DG ISSUES | DG ISSUES
DG canopy is rusted from front and bottom |  | DG ISSUES | DG ISSUES
Site main gate is rusted and damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shelter body is rusted (from Left-Top &amp; back side 20%) |  | CIVIL_WORK | SHELTER
DB door lock is broken due to rust and meter glass is also broken |  | CIVIL_WORK | Main DB
FE is expired |  | FIRE EXTINGUISER | EXPIRY
FE is missing |  | FIRE EXTINGUISER | EXPIRY
RECTIFIER NO. 1 IS ZERO BACK UP | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
FE is missing |  | FIRE EXTINGUISER | EXPIRY
FE is missing |  | FIRE EXTINGUISER | EXPIRY
A/C2 is not working | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
Site Battery Backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site fence not deployed so far while its material available at the site . |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
FE is missing |  | FIRE EXTINGUISER | EXPIRY
OD Cabinet door light is not available |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
OD Delta cabinet cooling system is faulty | HUW cabinet Door CLU Faulty | AIR_CONDITIONER | OD CABINET AIR CON
HT and cooling alarm loop due to Outdoor delta AC faulty |  | EXTERNAL ALARM | EXTERNAL ALARM
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Rectifier dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Site Battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Outdoor delta AC is faulty | HUW cabinet Door CLU Faulty | AIR_CONDITIONER | OD CABINET AIR CON
Delta cabinet Air filter need to replace | Delta Cabinet A/C Filter is damage | AIR_CONDITIONER | OD CABINET AIR CON
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Delta Cabinet Air con is faulty | Delta Cabinet A/C Filter is damage | AIR_CONDITIONER | OD CABINET AIR CON
OD Delta cabinet lock is faulty |  | DELTA CABINET | DOOR LOCK
HT and cooling alarm loop due to Outdoor delta AC faulty. |  | EXTERNAL ALARM | EXTERNAL ALARM
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Yellow label for site ID is missing |  | LABELING | LABELING
Meter box glass is broken |  | CIVIL_WORK | Main DB
Power meter box door is damaged |  | CIVIL_WORK | Main DB
AC cover outdoo unit | OD unit front cover is damage | AIR_CONDITIONER | AIR CONTIONER ODU
rectifier module dummy missing |  | DUMMY MISSING | DUMMY MISSING
OD TDD cabinet battery back up is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Site Battery backup is zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Site main gate is fully rusted and damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Shelter body is rusted |  | CIVIL_WORK | SHELTER
Site Boundary fence is completely damaged |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
FE is missing |  | FIRE EXTINGUISER | EXPIRY
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Site Fence is having 1m2 cut |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
there is no ladder installed to access RT antenna and OD air con Units |  | DESIGN ISSUE | DESIGN ISSUE
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
Site main gate is completely damaged /OT is a host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Main gate lock is missing | Site main gate padlock is missing | PADLOCK | Padlock
Extra materials available at site premises ( GSM Antenna\'s) |  | EXTRA MATERIAL | EXTRA MATERIAL
Antenna water proofing is required | Antenna water proofing is required | CABLE DRESSING | Antenna
RT Ladder is rusted |  | CIVIL_WORK | Ladder
rectifier module dummy missing |  | DUMMY MISSING | DUMMY MISSING
There is no ladder installed to access RT antenna |  | DESIGN ISSUE | DESIGN ISSUE
Site ID label is missing |  | LABELING | LABELING
Ericsson PBC6500 is at site |  | DESIGN ISSUE | DESIGN ISSUE
FE is missing |  | FIRE EXTINGUISER | EXPIRY
OD cables arrangement action is required | OD cable not arranged properly | CABLE DRESSING | CABLE DRESSING
Shelter roxtech sealing is required |  | OTHERS | Others
Rect modules Dummy missing |  | DUMMY MISSING | DUMMY MISSING
OT is a host - Main Gate is open | Site main gate padlock is missing | PADLOCK | Padlock
Dismantled indoor shelter still exist at site premises |  | EXTRA MATERIAL | EXTRA MATERIAL
Main gate lock is missing -OT is a host | Site main gate padlock is missing | PADLOCK | Padlock
FE is missing |  | FIRE EXTINGUISER | EXPIRY
Cabinet is dusted | Cabinet need to clean and filter need to replace | AIR_CONDITIONER | OD CABINET AIR CON
Engine oil leakage available |  | DG ISSUES | DG ISSUES
Main gate is rusted and need to paint |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
TDD cabinet OD cables need to arrange properly | TDD Cabinet cable not arranged properly | CABLE DRESSING | CABLE DRESSING
TN Dummy missing |  | DUMMY MISSING | DUMMY MISSING
A/C2 is faulty | One A/C is faulty or not working properly | AIR_CONDITIONER | AIR_CONDITIONER
Emerson rectifier is working at the site |  | DESIGN ISSUE | DESIGN ISSUE
TDD OD cabinet BB is zero and ID Emerson rectifier BB is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
OD earth cable need to arrange | OD Earth cable not arranged properly | CABLE DRESSING | CABLE DRESSING
Access Ladder to RT antenna is disconnected from the top and need to fix &amp; main access Spiral ladder mesh cage is rusted . |  | CIVIL_WORK | Ladder
Fiber cables need to arrange properly | Fiber cables not arranged properly | CABLE DRESSING | Fiber
BTS Room Seepage required civil action |  | CIVIL_WORK | SHELTER
FE is expired service date |  | FIRE EXTINGUISER | EXPIRY
Site main gate is not available - OT is a host |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
Dismantled Emerson rectifier available at the site |  | EXTRA MATERIAL | EXTRA MATERIAL
Cable tray support concrete is damaged |  | CIVIL_WORK | FOUNDATION
shelter OD light is not working |  | ILLUMINATION LIGHT | ILLUMINATION LIGHT
Air con ID units cleaning is required | A/C ID units cleaning is required | AIR_CONDITIONER | AIR CONDITIONER IDU
tower access ladder concrete is loose and need to be fixed so require civil action on priority |  | CIVIL_WORK | FOUNDATION
Lightning rod cable is cut |  | GROUNDING | LIGHTNING SYSTEM
RRU connectors waterproofing is required and dismantled jumpers need to remove |  | CABLE DRESSING | CABLE DRESSING
Site Battery Backup is zero | Battery Backup is Zero/Dead | BATTERY BACKUP | BATTERY BACKUP
Cabinet need to clean and filter need to replace | Cabinet need to clean and filter need to replace | AIR_CONDITIONER | OD CABINET AIR CON
OD Delta cabinets Locks are faulty |  | DELTA CABINET | DOOR LOCK
Tower paint is required |  | CIVIL_WORK | TOWER
Shelter door lock is faulty |  | CIVIL_WORK | SHELTER DOOR
Shelter body is partially rusted |  | CIVIL_WORK | SHELTER
power Meter box door glass is missing |  | CIVIL_WORK | Main DB
Customer link power is connected directly with AC |  | DESIGN ISSUE | DESIGN ISSUE
Minor housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Cisco Device is connected directly with AC |  | DESIGN ISSUE | DESIGN ISSUE
Himoinsa SDG is on off mode |  | DG ISSUES | DG ISSUES
Minor housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Shelter door lock is faulty |  | CIVIL_WORK | SHELTER DOOR
OD units pipes isolation is required | A/C OD pipes isolation is required | AIR_CONDITIONER | AIR CONTIONER ODU
1m wire mesh is cut and need to maintain to avoid any illegal access to the site premises |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
one sector pole grounding is cut |  | GROUNDING | ANTENNA GROUNDING
OD cables need to be arranged properly on cable tray and dismantled Ethernet cables need to remove | OD cable not arranged properly | CABLE DRESSING | CABLE DRESSING
Shelter body is having rusty parts |  | CIVIL_WORK | SHELTER
Shelter roxtech sealing is required |  | OTHERS | Others
Main gate is rusted |  | CIVIL_WORK | Fence / Boundry Wall / Main Gate
site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Shelter body is partially rusty |  | CIVIL_WORK | SHELTER
OD units are rusted | Both A/C ODU is Rusty | AIR_CONDITIONER | AIR CONTIONER ODU
Power meter box is rusted |  | CIVIL_WORK | Main DB
TN Dummy is missing |  | DUMMY MISSING | DUMMY MISSING
there is no access ladder installed for room OD Air con unit maintenance |  | DESIGN ISSUE | DESIGN ISSUE
TN Dummy missing |  | DUMMY MISSING | DUMMY MISSING
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Power meter box is rusted |  | CIVIL_WORK | Main DB
TDD cabinet battery backup is weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
A/C WATER LEAKAGE IS OBSERVED | LEAKAGE OBSERVED IN ODU AC | AIR_CONDITIONER | LEAKAGE
Lighting rod Cable stolen(45M) |  | GROUNDING | GROUNDING
Aircon panel unable to open due to wrong installation of OG Rectifier |  | DESIGN ISSUE | WRONG INSTALLATION
EXTRA MATERIAL (vsat dish, modem, inverter, RRN) |  | EXTRA MATERIAL | EXTRA MATERIAL
AC-1 Complete unit faulty(LG) | A/C compressor is faulty | AIR_CONDITIONER | Compressor
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HouseKeeping
Tower rod grounding cable is missing(50M) |  | GROUNDING | GROUNDING
Site housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | HouseKeeping
Tower rod grounding cable is missing(40M) |  | GROUNDING | GROUNDING
Tower rod grounding cable is missing(30M) |  | GROUNDING | GROUNDING
Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Battery backup is weak(AGISSON 12V 200AH,8 CELLS) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
TOWER LIGHTNING PROTECTOR ROD ground cable missing(30M) |  | GROUNDING | GROUNDING
Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
Housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
TOWER LIGHTNING PROTECTOR ROD ground cable missing(30M) |  | GROUNDING | GROUNDING
Battery backup is weak(SHOTO 200AH,8 CELLS) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Extra material(dimantled mw dish,1 on tower & 1 on ground) |  | EXTRA MATERIAL | EXTRA MATERIAL
Extra material(ATN CABINET) |  | EXTRA MATERIAL | EXTRA MATERIAL
Delta AC IS FAULTY |  | DELTA CABINET | DELTA _AIRCON FAULTY
Extra material(dimantled RF Antenna kept under OO shelter, belongs to OT) |  | EXTRA MATERIAL | EXTRA MATERIAL
Weak battery backup(8 cells 190ah) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Tower rod grounding cable is stolen-30m |  | GROUNDING | GROUNDING
AC1 COMPRESSOR FAULTY(PISTON,1.5T, GENERAL) | AC COMPRESSOR FAULTY(PISTON,21.5T,General) | AIR_CONDITIONER | Compressor
housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
WEAK BACKUP OF RT SEC A,B,C(12 CELLS, 40AH) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
1 BANK IS MISSING IN APM(100AH) |  | BATTERY BACKUP | BATTERY BACKUP
WRONG INSTALLATION AND LOW SPACE FOR AC ODU MAINTAINANCE |  | DESIGN ISSUE | DESIGN ISSUE
HOUSEKEEPING REQUIRED(TREE INSIDE BOUNDRY WALL) | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
Compound damaged DUE TO RAINFALL |  | CIVIL_WORK | Compound Damage
Battery back up of site is Weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Battery back up of site is Weak | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
HOUSEKEEPING REQUIRED | Site Housekeeping is required | HOUSEKEEPING | HOUSEKEEPING
housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
WEAK BATTERY BACKUP(8 CELLS 190AH) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP OF RT SECTORS A,B(8 CELLS 40AH) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP(4 CELLS 190AH) | One BB string is weak | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP(8 CELLS 190AH) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
WEAK BATTERY BACKUP(8 CELLS 190AH) | BB is weak. | BATTERY BACKUP | BATTERY BACKUP
Delta Cabinet filter not ok |  | DELTA CABINET | Delta_Filter
housekeeping is required | Site Housekeeping is required | HOUSEKEEPING | Housekeeping
A/C OD Units | Both A/C ODU is Rusty | AIR_CONDITIONER | AIR CONTIONER ODU

## Sheet4
MAIN_CATEGORY
AIR_CONDITIONER
AVIATION_LIGHT
BATTERY BACKUP
BREAKER/RELAY/SENSOR
CABLE DRESSING
CIVIL_WORK
COW
DELTA CABINET
DESIGN ISSUE
DG ISSUES
DUMMY MISSING
Emergency Light
EXTERNAL ALARM
EXTRA MATERIAL
FIRE EQUIPMENT
FIRE EXTINGUISER
GROUNDING
HOUSEKEEPING
ILLUMINATION LIGHT
LABELING
LOG BOOK
OD CABINET
OTHERS
PADLOCK
RECTIFIER
Wrong Installation
SUB CATEGORY
CABLE DRESSING
SHELTER
SHELTER DOOR
AC SPD FAULTY
ACDB
Air Con Sensor
AIR CONCITIONER
Air Conditioner
AIR CONDITIONER ID
AIR CONTIONER
AIR CONTIONER OD
Antenna
ANTENNA GROUNDING
Antenna Pole
Aviation Light
AVIATION LIGHT BOARD
AVIATION_LIGHT
AVR
BATTERY BACKUP
Cable Tray
Cables
CIVIL_WORK
Compound
Compound Damage
Compressor
COMPRESSOR 2.5 Rotary
COW
COW tyre
CPRI
DB
DELTA _AIRCON FAULTY
Delta Cabinet
DELTA RECTIFIER
Delta_Filter
DESIGN ISSUE
Designe Issue
DG
DG ISSUES
DOOR LOCK
Door Sensor
DUMMY MISSING
Emergency Light
Emergency Light
EXPIRY
EXTERNAL ALARM
EXTERNAL ALARMS
EXTRA MATERIAL
FACP BATTERY
Fence / Boundry Wall / Main Gate
Fiber
Filter
Fire Equipment
Fire Panel
FIRE PANEL
Fire Panel Battery
Foundation
Fuel
GROUNDING
House Keeping
HOUSEKEEPING
Housekeeping
HOUSEKEEPING/Omantel
huawei ETP48300 Display
IF
ILLUMINATION LIGHT
Indoor Shelter
LABELING
Ladder
Ladder Broken
Ladder Broken
LEAKAGE
LIGHTNING SYSTEM
LOG BOOK
LOGO TIMER
LOGOTIMER
Main DB
Main Gate
Maing DB
Microwave Antenna
MISSING
OD CABINET AIR CON
OTHERS
PADLOCK
PADLOCK/Omantel
Paint Job
PATHWAY DAMAGE
PCB Kit
Power Cable
Power connection
Rectifeir Module
RECTIFIER
RECTIFIER ALARMS
Rectifier Module
RECTIFIER MODULE
REMOTE
Remote Batteries
REMOTE MISSING
RT Ladder
Sand
sector blockage
Sensor
Shelter
Smoke Sensor
Sun Shade
TDD/WiMax
TEMPERATURE SENSOR
Tower
Tower Light
UNSAFE LADDER
VSAT
WRONG INSTALLATION
SUB CATEGORY
AIR_CONDITIONER
AIR CONTIONER ODU
OD CABINET AIR CON
Compressor
REMOTE MISSING
Control Panel
Remote Batteries
Sensor
PCB Kit
LEAKAGE
LOGO TIMER
DRAINAGE
AIR CONDITIONER IDU
Hand Mode
Condensor